## Sheet1
CHAPTER 10
Protection Problems
with Solutions
Problems |  | Topics
10.1 |  | Overcurrent relay-Time of operation
10.2 |  | Transformer- differential protection
10.3 |  | Transformer- differential protection-CT Ratios
10.4 |  | Circuit breaker ratings
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.10.1 | Overcurrent relay: time of operation
Explain how would you use an overcurrent characteristic to determine its time of operation,
given the following information:
Relay specification: 1A, 3sec
Plug setting: 125%
Time multiplier setting:.6
Current transformer ratio:400/1
Fault current: 4000A
Solution: | C.T Ratio |  | 400
| Fault current |  | 4000 | A
| Pilot wire current |  | = Fault current/C.T Ratio = Relay coil current
| Pilot wire current |  | 10 | A
| Plug setting |  | 1.25
Normal relay coil curren t= rated current * Plug setting=1*1.25=1.25A
| Plug setting multiplier |  | =Pilot wire current/Plug setting
8
i.e. Relay fault current as a multiple of plug setting =10/1.25=8
|  | Time, secs |  | Time multiplier setting=1
3.3
8
Plug setting multiplier
From the relay curve, the time of operation is 3.3 for a time setting of 1
| Operating time for TMS=1 |  |  | 3.3 | sec
| Given TMs |  |  | 0.6
Actual operating time =operating time for TMS=1*given TMS
|  |  |  | 1.98 | sec | Answer
Top of Page
Prob.10.2 | Transformer- differential protection
A 3-phase delta-star-connected 30 MVA 33/11 kV transformer is protected by a differential
relay. Calculate the relay current setting for faults drawing up to 200 per cent of the rated
current. The CT current ratio on the primary side is 500:5 and that on the secondary side
is 2000:5.
Solution: | MVA | rating |  | 30 | MVA
| kV1 | High side |  | 33 | kV
| kV2 | Low side |  | 11 | kV
| Ip | Primary line current |  | =MVA*1000/(1.73*kV1)
| Ip |  |  | 525.4861 | A
| Is | Sec.line current |  | =3*Ip
|  |  |  | 1576.4582 | A
| CT1 ratio | primary side |  | 100
| CT2 ratio | Sec.side |  | 400
| C.T current on primary side,I1 |  |  | =Ip/CT1 ratio
|  |  |  | 5.2549 | A
| C.T current on sec.side,I2 |  |  | =1.73*Is/CT2 rating
|  |  |  | 6.8263 | A
Relay current at 200 % of rated current
=2*(I2-I1)
|  |  |  | 3.1428 | A | Answer
Top of Page
Prob.10.3 | Transformer- differential protection-CT Ratios
A 3-phase delta-star connected 30MVA,132/33 kV transformer is protected by current
transformers>Determine the cT ratios for differential protection such that the circulating
current( through the transformer delta)does not exceed 5 A
Solution: | HV | L-L |  | 132 | kV
| LV | L-L |  | 33 | kV
| MVA |  |  | 30 | MVA
| I delta | Line value |  | MVA*1000/(1.73*HV)
|  |  |  | 131.3715 | A
| Istar | Line value |  | MVA*1000/(1.73*LV)
525.4861
| Ic | Circulating current |  | 5 | A
The CTs on the HV side are connected in star. Therefore '
| CT ratio | HV side |  | 105.0972 |  | Answer
CTs are connected in delta on the LV side. Therefore,
| CT ratio | LV side |  | =131.37(5/1.73)
|  |  |  | 379.6865 |  | Answer
Top of Page
Prob.10.4 | Circuit breaker ratings
A circuit breaker is rated at 1000A, 1200 MVA,33 kV,3 sec, 3-phase oil-circuit breaker.
(I) the rated normal current
(ii) breaking capacity
(iii) rated symmetrical breaking current
(iv) rated making capacity
(v) short-tme rating
(vi) rated service voltage
Solution:
| I |  |  |  | 1000 | A
| MVA |  |  |  | 1200
| kV |  |  |  | 33
| (I) |  |  |  | 1000 | A | Answer
| (ii) |  |  |  | 1200 | MVA | Answer
| (iii) | =MVA*1000/1.73*kV= |  |  | 21019.443 | A(rms) | Answer
| (iv) | max.value of asymmetrical current=2.55 * rated symm. Breaking current
[5 empty] | 53599.5796 | A | Answer
| (v) | same as rated symm.breaking current
[5 empty] | 21019.443 | A for 3 seconds |  | Answer
| (vi) |  |  |  | 33 | kV | Answer
Top of Page