## Sheet1
CHAPTER 11
Steady-state stability Problems
with Solutions
Prob. No: |  | Topic
11.1 | Frequency of rotor oscillations for small disturbance
11.2 | Steady -state stability limit of a generator connected to an infinite bus via parallel lines
11.3 | Steady-state stability of a system with & without a shunt reactor
11.4 | Steady -state stability of a generator connected to an infinite bus via a line with a resistive
load connected halfway-Example 1
11.5 | Steady -state stability of a generator connected to an infinite bus via a line with a resistive
load connected halfway-Example 2
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.11.1 | Frequency of rotor oscillations for small disturbance
A synchronous generator of reactance 1.5 pu is connected to an infinite busbar (V=1 pu)
through a line and transformer of total reactance 0.5 pu. Thye no-load voltage of the
generator is 1.2 pu and the inertia constant H= 3.1416 MW-sec per MVA. Resistance &
damping may be neglected.Calculate thre frequency of the oscillations set up when the
operates at load angle of 60 deg. and is subjected to a small disturbance.
Solution: | Xg |  |  | 1.5 | pu
| Xline & Transformer |  |  | 0.5 | pu
| X | Total |  | 2 | pu
| d0 |  |  | 60 | deg
| E |  |  | 1.2 | pu
| V |  |  | 1 | pu
| dp/dd | =EV Cos d/X |  | 0.30028
| G |  |  | 1 | MVA
| H |  |  | 3.1416
| f |  |  | 50 | Hz
| M | GH/(3.1416*f) |  | 0.02
| p1,2 | roots |  | =+-jsqrt((dp/dd0)/M)
|  |  | +-j | 3.8748 | rad/s
|  |  |  | 0.61669 | Hz | Answer
Top of Page
Prob.11.2 | Steady -state stability limit of a generator connected to an infinite bus via parallel lines
A 3-phase generator tarnsformer set is connected to an infinite busbar via duplicate lines.
and the steady-state stability limit is 200 MW.This limit is reduced to 70 MW during a
3-phase short-circuit midway along one-line. Calculate the pu reactance on a base of 100
MVA of the generator-transformer and of each line, and the power limit when the faulty line
is isolated.
What reasonable assumptions must be made regarding the system emf's?
Solution: |  | Two lines in parallel
[5 empty] | X2 |  | E2
|  | E1 | X1
X2
One line faulted
X2
X1
|  |  |  | X2/2 | X2/2
|  |  | a |  |  | c
X2
X1
|  |  |  | X2/2 | X2/2
b
Convert star abc into delta
|  |  |  | 3X1+X2 |  |  |  | X2/2
| E1 |  |  | 1 | pu
| E2 |  |  | 1 | pu
Unfaulted lines -Reactance between E1 & E2
=X1 + (X2/2)
One line faulted-Reactance between E1 & E2
=3X1 +X2
Steady state stability - unfaulted lines
|  |  |  | 200 | MW
| Pmax1 |  |  | 2 | pu | on 100 MVA base
Steady state stability -faulted line
|  |  |  | 70 | MW | on 100 MVA base
| Pmax2 |  |  | 0.7 | pu
Therefore,
| X1+ (X2/2) | =E1E2/Pmax1 |  | 0.5 | pu | Eq.1
| 3X1 +X2 | =E1E2/Pmax2 |  | 1.4286 | pu | Eq.2
Rewrite Eqs.1 &2:
| 3X1 +1.5X2 |  | = | 1.5 | pu | Eq.3
| 3X1+X2 |  | = | 1.4286 | pu | Eq.4
Subtract (4) from (3):
| .5X2 |  | = | 0.071429
| X2 |  | = | 0.14286 | pu | Answer
From Eq.4, we get
| X1 |  | = | 0.42857 | pu | Answer
Power limit when the faultynline s isolated:
| Pmax3 |  | = | E1*E2/(X1+X2)
|  |  |  | 1.75 | pu
|  |  |  | 174.9999 | MW | Answer
Top of Page
Prob.11.3 | Steady-state stability of a system with & without a shunt reactor
Calculate the steady-state power limit of the following system in pu and in MW with and
without the reactor connected.
pu
|  | XT= | 0.1 | pu | XT= | 0.1 | pu Em= | 1
| G |  |  | Xl= | 0.2 |  |  | M
pu
Eg= | 1.2 | pu |  |  |  | Xm= | 1 | pu
| Xg= | 1 | pu
|  | Static Reactor |  | X= | 1 | pu
| All pu reactances are expressed on |  |  |  | 10 | MVA Base
Solution: | Without Reactor:
Pmax = Eg*Em/(Xg+XT+Xl+XT+Xm)
|  |  |  | 0.5 | pu
|  |  |  | 5 | MW | Answer
With Reactor:
| G |  |  |  | M
| Xg + XT |  |  |  | Xl + XT + Xm
X
Convert the T -circuit into an equivalent PI-circuit
| G |  |  | M
Xeq
Xeq =(Xg + XT)+(Xl + XT + Xm)+(Xg + XT)*(Xl + XT + Xm)/X
|  |  |  | 3.83 | pu
| Pmax = Eg*Em/Xeq |  |  | 0.31332 | pu
|  |  |  | 3.1332 | MW | Answer
Top of Page
Prob.11.4 | Steady -state stability of a generator connected to an infinite bus via a line with a
resistive load connected halfway-Example 1
The figure below shows a power system and its reactance diagram.
Line
Line
Infinite
| Generator bus |  | S |  | bus
Load bus
Resistive
load
| E.g. | [5 empty] | Infinite bus
V
| Xg = | 0+1j
pu
|  | Xl= | 0+.2j | S | 0+.2j
|  |  | pu |  | pu
R
| Voltage of infinite bus is = |  |  | 1 | pu
| With S open , the complex power delivered to the infinite bus is = | [5 empty] | .8+.6j | pu
| S is then closed through a load resistance |  |  |  | R= | 0.8 | pu.
At the same time generator excitation is kept constant and mechanical power input
| the generator is increased to maintain the power input to the infinite bus at | [6 empty] | 0.8
pu. Determine whether the steady-state stability limit is reached
Solution: | S open:
| Voltage of infinite bus=V= |  |  | 1+0j | pu | Vabs= | 1
| Current into infinite bus = |  |  | I
| Power into infinite bus = |  |  | .8+.6j
| Conjugate Power |  |  | 0.8-0.6j
| Therefore, I= |  |  | 0.8-0.6j
Eg = V+I*(Xg + Xl + Xl)
| IMSUM(Xg + Xl + Xl) |  |  | 1.4j
| ImPRODUCT(I, IMSUM(Xg + XL + Xl) |  |  | 0.84+1.12j
| Eg = V+I*(Xg + Xl + Xl) |  |  | 1.84+1.12j
| IMABS(E.g.)= |  |  | 2.1541
| Egangle |  |  | 31.3446 | deg
S closed:
E.g. remains constant, and the circuit becomes
|  | E.g. | [5 empty] | Infinite bus
V
|  | Xg= | 0+1j
pu
|  |  | Xl= | 0+.2j | S | 0+.2j
|  |  |  | pu |  | pu
|  |  |  | R= | 0.8+0j | pu
A, B constants of the T-network are:
A=1+(Xg + Xl)/R
| (Xg + Xl) |  |  | 1.2j
|  |  | = | 0+1.2j
| (Xg + Xl)/R |  |  | 1.5j
| A |  | = | 1+1.5j | Real = | 1 | I= | 1.5
| Aabs |  |  | 1.8028
| Aangle | a |  | 56.3385 | deg
B=Xg+2Xl+(Xg*Xl)/R
| Xg*Xl |  |  | -0.24
| Xg*Xl/R |  |  | -0.3
| Xg+2*Xl |  |  | 1.4j
| B= |  |  | -0.3+1.4j | Real = | -0.3 | I= | 1.4
| Babs |  |  | 1.4318
| Bangle | b |  | 102.0552 | deg
Pmax =(Eg*V- Aabs Cos(b-a))/Babs
|  |  |  | 0.62498 | pu
The desired delivery of power of .8 pu to the infinite bus cannot be met. System is unstable
| beyond | 0.6249 | pu
Top of Page
Prob.11.5 | Steady -state stability of a generator connected to an infinite bus via a line with a
| resistive | load connected halfway-Example 2
Determine whether delivery of power of .8 pu to the infinite bus of the system for Prob.11.4
is possible if the load resistance is 1.25 pu.
Solution: |  | E.g. | [5 empty] | Infinite bus
V
|  | Xg= | 0+1j
pu
|  |  | Xl= | 0+.2j | S | 0+.2j
|  |  |  | pu |  | pu
|  |  |  | R= |  | 1.25+0j | pu
A, B constants of the T-network are:
A=1+(Xg + Xl)/R
| (Xg + Xl) |  |  | 1.2j
|  |  | = | 0+1.2j
| (Xg + Xl)/R |  |  | 0.96j
| A |  | = | 1+0.96j | Real = | 1 | I= | 0.96
| Aabs |  |  | 1.3862
| Aangle | a |  | 43.8531 | deg
B=Xg+2Xl+(Xg*Xl)/R
| Xg*Xl |  |  | -0.24
| Xg*Xl/R |  |  | -0.192
| Xg+2*Xl |  |  | 1.4j
| B= |  |  | -0.192+1.4j | Real = | -0.192 | I= | 1.4
| Babs |  |  | 1.4131
| Bangle | b |  | 97.7673 | deg
Pmax =(Eg*V- Aabs Cos(b-a))/Babs
|  |  |  | 0.94618 | pu
Pmax is greater than .8 pu. Hence
power of .8 pu to the infinite bus can still be maintained when the load resistance is 1.25
pu.
Top of Page