## Sheet1
Chapter 17
Per Unit Systems Problems
with Solutions
Problem |  | Topic
17.1 |  | pu problem
17.2 |  | pu problem
17.3 |  | pu problem
17.4 |  | pu problem
17.5 |  | pu problem
17.6 |  | pu problem
17.7 |  | pu problem
17.8 |  | pu problem
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.17.1
A portion of a power system consists of two generators in parallel connected
to a step-up transformer that links them to a 230 kV transmission line. the ratings of these
components are :
Generator 1: 10 MVA, X = 10%
Generator 2: 5MVA, X = 8%
Transformer: 15 MVA, X = 6%
Transmission line:230 kV, 4 + j 60 Ohms
Express the reactances and the impedance in % with 15 MVA as the base value.
Solution: | Generator 1:
| X% on generator rating |  |  | 10
| MVA rating of generator |  |  | 10
| Common base MVA selected |  |  | 15
| X% on common base |  |  | =X% on generator rating*Commomn base selected/Mva rating of-
|  |  |  | 15 | % | Answer |  | generator
Generator 2:
| X% on generator rating |  |  | 8
| MVA rating of generator |  |  | 5
| Common base MVA selected |  |  | 15
| X% on common base |  |  | =X% on generator rating*Commomn base selected/Mva rating of-
|  |  |  | 24 | % | Answer |  | generator
Transformer
| X% on transformer rating |  |  | 6
| MVA rating of transformer |  |  | 15
| Common base MVA selected |  |  | 15
| X% on common base |  |  | =X% on transformer rating*Commomn base selected/Mva rating of
|  |  |  | 6 | % | Answer |  | transformer
Transmission Line:
| Line R |  |  | 4 | ohms
| Base kV |  |  | 230 | kV
| Line % R |  |  | =Line R in Ohms*Base MVA*100/((base kV)*(basekV))
|  |  |  | 0.11342 |  | Answer
| LineX |  |  | 60 | ohms
| Base kV |  |  | 230 | kV
| Line % X |  |  | =LineX in Ohms*Base MVA*100/((base kV)*(basekV))
|  |  |  | 1.7013 |  | Answer
Top of page
Prob.17.2
Draw the pu reactance diagram for the system shown below:
G2
| G1 | T1 | Line | T2 |  |  | G3
T3
Load
| G1 | 11kV,20MVA,15%
| T1 | 11/66kV,30MVA,15%
| Line | j60 ohms
| T2 | 66/11kV,30MVA,15%
| G2 | 11kV,10MVA,10%
| G3 | 11kV,10MVA,10%
| T3 | 11/6.6 kV,2.5 MVA,8%
Choose a base of 20MVA,66kV
Solution: | Base MVA |  |  | 20 | MVA
| G1: | X |  | 0.15 | pu | on rated MVA
| G2: | X |  | 0.1 | pu | on rated MVA
| G3 | X |  | 0.1 | pu | on rated MVA
| G1: | Rated MVA |  | 20 | MVA
| G2: | Rated MVA |  | 10 | MVA
| G3 | Rated MVA |  | 10 | MVA
| T1: | X |  | 0.15 | pu | on rated MVA
| T2: | X |  | 0.15 | pu | on rated MVA
| T3: | X |  | 0.08 | pu | on rated MVA
| T1: | Rated MVA |  | 30 | MVA
| T2: | Rated MVA |  | 30 | MVA
| T3: | Rated MVA |  | 2.5 | MVA
We now calculate reactances on base MVA
=Base MVA*X/rated MVA
| G1: | X |  | 0.15 | pu
| G2: | X |  | 0.2
| G3 | X |  | 0.2
| T1: | X |  | 0.1
| T2: | X |  | 0.1
| T3: | X |  | 0.64
| Line: | X ohms |  | 60
|  | Base kV |  | 66
|  | Xpu |  | =X ohms*Base Mva/((Base kV)*(Base kV))
0.27548
Reactance diagram:
|  | G1 |  |  | G2 | G3
|  |  | T1 | Line | T2
T3
Prob.17.3
Draw a per unit impedance diagram for the system described below. Choose a base kVA of 50
Two generators G1 and G2 are in parallel and are connected to a generator transformer T1
which in turn is connected to a transmission line L. At the receiving end of the line is
connected a transformer T2 , the secondary of which is connected to a motor M.
The equipment ratings are given below:
| G1 | 10kVA.2500V,X=.2 pu
| G2 | 20kVA,2500V,X=.3pu
| T1 | 40kVA,2500/8000V,X=.1pu
| T2 | 80kVA,10000/5000V,X=.09pu
| Line | 50+j200 ohms
| M | 25kVA,4000V,X=.1 pu
Solution: | Base kVA |  |  | 50 | kVA
| G1: | X |  | 0.2 | pu | on rated kVA
| G2: | X |  | 0.3 | pu | on rated kVA
| G1: | Rated kVA |  | 10 | kVA
| G2: | Rated kVA |  | 20 | kVA
| T1: | X |  | 0.1 | pu | on rated kVA
| T2: | X |  | 0.09 | pu | on rated kVA
| T1: | Rated kVA |  | 40 | kVA
| T2: | Rated kVA |  | 80 | kVA
| M: | X |  | 0.1 | pu
| M: | Rated kVA |  | 20 | kVA
We now calculate reactances on base kVA
=base kVA*X/rated kVA
| G1: | X |  | 1 | pu | Answer
| G2: | X |  | 0.75 | pu | Answer
| T1: | X |  | 0.125 |  | Answer
For T2, we calculate the reactance on base kVA and base kV
=(Base kVA*X/rated kVA)*(Rated kV/Base kv)*(Rated kV/Base kV)
| Rated kV |  |  | 10 | kV
| Base kV |  |  | 8 | kV
| T2: | X | pu | 0.087891 | pu | Answer
| Line: | R ohms |  | 50 | ohms
|  | X ohms |  | 200 | ohms
|  | Base kV |  | 8 | kV
|  | Rpu |  | =R ohms*(Base kVA/1000)/((Base kV)*(Base kV))
|  |  |  | 0.039062 | pu | Answer
|  | Xpu |  | =X ohms*(Base kVA/1000)/((Base kV)*(Base kV))
|  |  |  | 0.15625 | pu | Answer
| M: | X | pu | 0.25 | pu | Answer
Impedance diagram:
j1 pu
G1
|  |  | j.125 pu | .039 pu | j.156pu | j.088 pu | j.25 pu | M
j.75 pu
G2
Top of page
Prob.17.4
A 3-phase 13 kV transmission line delivers 8 MVA of load .The per phase impedance of
the line is .01 +j .05 pu referred to 13 kV, 8 MVA base. What is the voltage drop across
the line?
Solution: | Base MVA |  |  | 8 | MVA
| Base kV |  |  | 13 | kV
| Base current |  |  | = base MVA*1000/(1.73*Base kV)
|  |  |  | 355.7137 | A
| New base MVA/phase |  |  | 2.666 | MVA
| New Base kV/phase |  |  | 7.5145 | kV
| New Base current |  |  | 355.7137 | A
| R |  |  | 0.01 | pu
| X |  |  | 0.05 | pu
| Rpu, new | =R*(Base KV/New BaseKV/phase)*(Base kV/New BaseKV/phase)*(New Base
|  | MVA/Base MVA)= |  | 0.0099738 | pu
| Xpu, new | =X*(Base KV/New BaseKV/phase)*(Base kV/New BaseKV/phase)*(New Base
|  | MVA/Base MVA)= |  | 0.049869 | pu
| Base Z new |  |  | = New Base kV /phase*1000/New Base current
|  |  |  | 21.125 | ohms
| Actual R |  |  | =Rpu,new*Base Z new
0.2107
| Actual X |  |  | =Xpu,new*Base Z new
1.0535
| =I*(Actual R) |  |  | 74.9479 | Volts
| =I*(ActualX) |  |  | 374.7396 | Volts
| Voltage drop/phase |  |  | 75 + j 375 | Volts | Answer
Top of page
Prob.17.5
A 3-phase item of equipment is rated at 800kVA,11kV and has an impedance of 10%
referred to its voltage.
(I) Is 800 kVA understood to be its per-phase or 3phase power rating?
(ii) Is 11 kV understood to be its phase-to-neutral or phase-to-phase voltage rating?
(iii) What is the impedance of the equipment in ohms?
Solution: | (I) | 3-phase
| (ii) | phase-phase
| (iii) | kVAbase |  | 800
|  | kVbase |  | 11
|  | Ibase |  | 42.0389
|  | Ibase |  | 42.0389 | A
|  | Zbase |  | =kVbase*1000/(1.73*Ibase)
|  |  |  | 151.25 | ohms
|  | Zpu |  | 0.1
|  | Z |  | 15.125 | ohms | Answer
Top of page
Prob.17.6
The reactance X of a generator is given as 0.2 pu based on the generator's nameplate
rating of 13.2 kV,30 MW. The base for calculations is 13.8 kV,50 MW. Find X on this new
base.
Solution: | Xpu old |  |  | 0.2
| base MVA old |  |  | 30
| base MVA new |  |  | 50
| base kV old |  |  | 13.2 | kV
| base kV new |  |  | 13.8 | kV
| Xpu new |  |  | = Xpu old*base MVA new*Base KV old*Base kV old/
(baseMVA old*base kV new *base kV new)
|  |  |  | 0.30498 | pu | Answer
Top of page
Prob.17.7
In the power system shown below:
M1
| G | T1 | Line | T2 |  |  | M2
| G1 | 13.8kV,30MVA,15%
| T1 | 13.2kVdelta/115kVstar,35MVA,10%
| Line | j80 ohms
| T2 | three 1-phase transformers each rated 12.5/67kV,10MVA,10%
| M1 | 12.5kV,20MVA,20%
| M2 | 12.5kV,10MVA,20%
Draw the reactance diagram with all reactances marked in pu.
Select the generator rating as base in the generator circuit.
Solution: | T2:
| MVA | 3-phase |  | 30 | Mva
| Vp | L-L voltage primary |  | 12.5 | kV
| Vs | L-L voltage secondary |  | 115.91 | kV
| X |  |  | 0.1 | pu
| T1: |  |  | 0.1 | pu
| MVA | 3-phase |  | 35 | Mva
| Vp' | L-L voltage primary |  | 13.2 | kV
| Vs' | L-L voltage secondary |  | 115 | kV
| X |  |  | 0.1 | pu
A base of 30 MVA ,13.8 kV in the generator circuit requires a 30 MVA base in all parts of
the circuit and the folllowing voltage bases.
| G1: | kV | base | 13.8 | kV
|  | MVA | base | 30 | MVA
|  | X |  | 0.15 | pu
| Line: |  |  | =13.8*115/13.2=
|  |  |  | 120.2273 | kV
| Motors: |  |  | =120*Vp/Vs=
|  |  |  | 12.9411 | kV
Transformer reactances converted to proper base are:
T1:
| X |  |  | .1*(30/35)*(13.2*13.2/(13.8*13.8))
|  |  |  | 0.078423 | pu
T2:
| X |  |  | =.1*12.5*12.5/(12.941*12.941)
|  |  |  | 0.0933 | pu
Line:
| base X |  |  | =120.2273*120.2273/30
|  |  |  | 481.8199 | ohms
| X |  |  | 80 | ohms
| Xpu |  |  | 0.16604 | pu
M1:
|  | kV |  | 12.5
|  | MVA |  | 20
| X | own base |  | 0.2 | pu
|  | new base |  | =.2*(30/20)*(12.5*12.5/(12.941*12.941)
|  |  |  | 0.2799 | pu
M2:
|  | kV |  | 12.5
|  | MVA |  | 10
| X | own base |  | 0.2 | pu
|  | new base |  | =.2*(30/10)*(12.5*12.5/(12.941*12.941)
|  |  |  | 0.5598 | pu
Reactance diagram:
All values in pu
|  |  | G1 |  |  | M1 | M2
|  |  | 0.15 |  |  | 0.28 | 0.556
|  |  |  | T1 | Line | T2
|  |  |  | 0.078 | 0.166 | 0.093
Top of page
Prob.17.8 | A 15000 kVA, 8.5 kV 3-phase generator has a sub-transient reactance of 20 %. It is
connected through a delta-star transformer to a high voltage transmission line having
a total series reactance of 70 ohms. At the load end of the line is a star-star step-down
transformer. Both transformer banks are compose of single-phase transformers connected
for three-phase operation. Each of the three transformers composing each bank is rated
6667 kVA , 10-100 kV ,with a reactance of 10 %. The load represented as impedance is
drawing 10000 kVA at 12.5 kV and .8 pf lagging.
(I) Draw the one-line diagram and mark base kV in the three parts of the system. Choose a
base of 10000 kVA,12.5 kV in the load circuit
(ii) Draw the positive sequence impedance diagram showing all impedances in pu.
(iii) Determine the voltage at the terminals of the generator.
Solution:
| basekV= | 7.22 | basekV= | 125 |  | base kV=12.5
| G1 | T1 | Line | T2
Load
|  | delta/star |  | star/star
| Base kVA |  |  | 10000 | in load
| Base kV |  |  | 12.5 | in load
T1and T2:
single-phase units
| kVA | per phase |  | 6667
| kVA | 3-phase |  | 20001
| X |  |  | 0.1 | pu
| T | Turns Ratio |  | 0.1
| kV(L-L) | High side |  | 125 | kV
| kV(L-L) | Low side |  | 7.2169 | kV
| kV | single-phase-low side |  | 10 | kV
| X | on common base |  | =.1*(10000/(3*6667))*(10*1.73/12.5)*(10*1.73/12.5)
|  |  |  | 0.095768 | pu
G1:
| kVA |  |  | 15000
| kV |  |  | 8.5
| X'' |  |  | 0.2 | pu
| Base kV | =(125/1.73205)*(T) |  | 7.2169
| X''= | on common base |  | =X''*(base MVA/gen. MVA)*(genKV/base kV)*(genkV/base kV)
|  |  |  | 0.18496 | pu
Line:
| kV |  |  | 125
| X |  |  | 70 | ohms
| Base Z |  |  | =base kV*basekV/base MVA
|  |  |  | 1562.5 | ohms
| X | pu |  | 0.0448 | pu
Load:
| kVA |  |  | 10000
| kV |  |  | 12.5
| pf |  |  | 0.8 | lag
| Pload | pu |  | 0.8
| Qload | pu |  | 0.6
| I, load current, pu |  |  | =(P-jQ)/Vload
| Vload |  |  | 1 | pu
| Re I=P/Vload |  |  | 0.8
| Im I = Q/Vload |  |  | -0.6
| Rload |  |  | 0.8 | pu
| Xload |  |  | 0.6 | pu
Single-line diagram:
|  |  | G1 |  |  | 0.8
[7 empty] | Load | V=1 pu
Vt
|  |  | j.1845 |  |  | j.6
|  |  |  | j.096 | j.0448
|  |  | a | T1 | Line | T2 b
j.096
| Reactance a-b |  |  | 0.23634 | pu
Vt=1+(ReI+jImI)*(j*Reactance a-b)
| Re Vt=1-ImI*Reactance a-b |  |  | 1.1418
| Im Vt = Re I*Reactance a-b |  |  | 0.18907
| Vtmag |  |  | 1.1573 | pu
|  |  |  | 8.3525 | kV | Answer
Top of page