## Sheet1
CHAPTER1
D.C.Machine Problems
with Solutions
Problems |  |  | Sub-topics
1.1 |  |  | d.c.generator - back emf
1.2 |  |  | d.c machine-generator & motor action
1.3 |  |  | d.c. motor-ouput power & torque
1.4 |  |  | d. c. shunt motor-Effects of flux & torque on current and speed
1.5 |  |  | d.c.generator-long shunt compound
1.6 |  |  | d.c.generators-parallel operation
1.7 |  |  | d.c.generators in parallel-effect of changing the excitation of one
1.8 |  |  | d.c. motor- hysterisis & eddy current losses
1.9 |  |  | d.c. motor -efficiency
1.1 |  |  | universal motor
1.11 |  |  | d.c. motor- field weakening
1.12 |  |  | d.c.generator -Transient behaviour
1.13 |  |  | Fractional kW series moor
1.14 |  |  | Speed controller of a d.c motor
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.1.1 | DC generator-back emf
When a dc generator is being driven at 1200 RPM, the generated emf is 125 V. What
will be the generated emf if (a) the field flux is decreased by 10% with the speed
remaining unchanged ,and (b)if the speed is reduced to 1100 RPM ,the field flux
remaining unchanged ?
Solution: | (a)
|  | E1= | 125
|  | F1= | F1
|  | F2= | .9*F1
E2=E1*F2/F1=0.9*E1
|  |  | 112.5 | Volts | Answer
| (b) | N1= | 1200 | RPM
|  | N2= | 1100 | RPM
E2=E1*N2/N1=
|  |  | 114.5833 | Volts | Answer
Back to top of page
Prob.1.2 | d. c. generator- generator & motor action
A shunt machine has armature and field resistances of 0.04 ohm and 100 ohms
respectively. When connected to a460 V dc supply and driven as a generator at 600
RPM, it delivers 50 kW. Calculate it speed when running as a motor and
taking 50 kW from the same supply. Show that the direction of rotation of the machine
as a generator and as a motor under these conditions is unchanged.
Solution: | P1,Generator power = |  | 50000 | W
| V, terminal Voltage = |  | 460 | V
I, Generator line current=P1/V=
|  |  | 108.6957 | A
| I, Motor line current |  | 108.6957 | A
If2=Motor field current = V/Rf = generator field current
|  |  | 4.6 | A
Ia1,Generator armature current=I+If2=
113.2957
| Ra = |  | 0.04 | ohm
| Rf = |  | 100 | ohms
E1=Generator back emf=V+Ia1Ra
|  |  | 464.5318 | V
Ia2=Motor armature current=I-If2=
|  |  | 104.0957 | A
E2,Motor back emf=V-Ia2Ra=
455.8362
Speed is proportional to back emf.
| N1,Generator speed = |  | 600 | RPM
N2,Motor speed = N1(E2/E1)
|  |  | 588.7685 | RPM
The direction of field flux remains the same when operating as a motor or a generator.
However, the direction of the armature current changes in the two modes of operation.
Therefore, according to Fleming's Left hand Rule for motor operation and the Right-
Hand Rule for the generator operation, the direction of rotation is unchanged.
Back to top of page
Prob.1.3 | d. c. motor- output power & torque
A 240 V dc motor has an armature resistance of 0.68 ohm and draws a
a full-load current of 24 A at a speed of 100 RPM .Calculate(a) the back emf (b) the
output power developed, and(c) the torque developed.
Solution:
| V= |  | 240
| Ia = |  | 24
| Ra = |  | 0.68
| E, back-emf = V-IaRa = |  | 223.68 | Volts | Answer
P, power developed = E*Ia
|  |  | 5368.32 | Watts | Answer
| N, speed |  | 1000 | RPM
T,Torque=60*P/(2*3.1416*N)
|  |  | 51.2636 | N-m | Answer
Back to top of page
Prob.1.4 | d. c. shunt motor-Effects of flux & torque on current and speed
A shunt motor connected across a 440 V supply takes an armature current of 20 A and
runs at 500 RPM. The armature resistance is 0.6 ohms. If the magnetic flux is reduced
by 30 % and the torque developed by the armature increases by 40 % ,what are the
values of the armature current and of the speed?
Solution:
| V= |  | 440
| Ia1= |  | 20
| Ra = |  | 0.6
| E1=V-Ia1*Ra |  | 428 | Volts
| F1= |  | F1
| F2= |  | 0.7F1
E2=new back emf
| E2=E1*F2/F1=E1*0.7 |  | 299.6 | Volts | Answer
| T1,Original torque = |  | T1
| T2,New torque = |  | 1.4T1
Ia2=New current
| N1=original speed |  | 500 | rpm
| E1,original back emf |  | E1
T, Torque is proportional to E*Ia/N. Therefore
T2/T1= (E2/E1)(Ia2/Ia1)(N1/N2),or
Ia2/N2=(T2/T1)(Ia1/N1)(E1/E2)
|  |  | 0.08 |  | Eq.1
E2=V-Ia2Ra.Therefore,
| Ia2=(V-E2)/Ra = |  | 234 | Amps
E is proportional to F and N. Therefore
N2=N1(E2/E1)(F1/F2)=N1((V-Ia2Ra)/E1)(F1/F2)=
500((440-Ia2*.6)/428)*(1/0.7)
or,
| (440-Ia2*0.6)/N2= |  | 0.5992 |  | Eq.2
From equations 1 and 2,
| (440-Ia2*.6)/Ia2= |  | 7.49
or,
| Ia2= |  | 54.3881 | Amps
From Eq .1,
| N2= |  | 679.8517 | RPM | Answer
Back to top of page
Prob.1.5 | d.c.generator-long shunt compound
A 4 pole 500V 25 kW long-shunt compound generator delivers full-load at the rated
voltage.Calculate the emf generated, if the armature resistance is 0.03 ohm,series field
| resistance is .04 ohm, and the shunt field resistance |  |  |  |  | 200 ohm.Contact drop per brush
is .9 volts. Neglect armature reaction.
Solution:
|  |  | Shunt field | Ish
Series field
G
IL+Ish
IL
Load
| P | Generator power=
|  |  | 25000 | W
| V | Generator voltage=
|  |  | 500 | Volts
| IL | Load current=P/V
|  |  | 50 | A
| Rsh | Shunt field resistance=
|  |  | 200 | ohms
| Ish | shunt field current=V/Rsh
|  |  | 2.5 | A
| IL+Ish |  | 52.5 | A
| Rs | Series field resistance=
|  |  | 0.04 | ohm
Volt drop in series field=(IL+Ish)*Rs=
|  |  | 2.1 | V
| Ra | Armature resistance=
|  |  | 0.03 | ohm
Volt drop in armature=(IL+Ish)Ra=
|  |  | 1.575 | V
Volt drop in brushes=2*.9=
|  |  | 1.8 | V
Total voltage drop=2.1+1.575+1.8=
|  |  | 5.475 | V
| Terminal voltage= |  | 500 | V
Emf=terminal voltage +total voltage drop=
|  |  | 505.475 | V | Answer
Back to top of page
Prob.1.6 | d.c.generators-parallel operation
Two shunt generators run in parallel on a bus-bar and supply 1000 A to consumers.Each
machine has an armature resistance of .02 ohm and a field resistance of 30 ohms, the
emf's generated being 465 V and 460 V respectively. Calculate
(a) the output of each machine, and (b) the bus voltage
Solution: | Let
| V | Busbar voltage
| I1 | Machine 1 current
| I2 | Machine 2 current
| Rf | field resistance |  | 30 | ohms
| Total field current = |  |  | 2*V/Rf
| IL | load current |  | 1000 | A
| I1 +I2 |  |  | =IL+ (2*V/Rf) |  | Eq.1
| Ra |  |  | 0.02 | ohm
| E1 | back emf |  | 465 | Volts
| E2 | back emf |  | 460 | Volts
V=E1-I1*Ra=E2-I2*Ra from which
| I1 |  |  | =(E1-V)/Ra |  | Eq.2
| I2 |  |  | =(E2-V)/Ra |  | Eq.3
Substituting Eqs.2 &3 in Eq.1,
((E1-V)/Ra )+((E2-V)/Ra)= IL +(2*V/Rf)
from which,
| V |  |  | =(E1*Rf+E2*Rf-Rf*Ra*IL)/(2*RA+2*Rf)
|  |  |  | 452.1985 | Volts
| I1 |  |  | =(E1-V)/Ra
|  |  |  | 640.0733 | A
| I2 |  |  | =(E2-V)/Ra
|  |  |  | 390.0733 | A
Total current=640+390=1030 A=1000A of load & 30 A for the fields
Back to top of page
Prob.1.7 | d . c. generators in parallel-effect of changing the excitation of one
Four generators are paralleled on a 240 V bus-bar. all the machines share equally a load
of 800 A, the induced emf of each being 250V.
An operator inadvertently alters the position of a field regulator arm thereby increasing
the emf of one machine by 4 %. Calculate the current of each machine and state
whether any harm has been done.
Solution: | E1 | original emf of machine1 = |  |  | 250 | V
| E1' | new emf of machine1=E1+.04*E1'= |  |  | 260 | V
| Ia1 | current of machine1 |  |  | =800/4 | A
| Ia1 |  |  |  | 200 | A
| V | busbar voltage |  |  | 240 | V
| Ra | armature resistance
Ia1Ra=E1-V. Therefore,
| Ra |  |  |  | =(E1-V)/Ia1=
[5 empty] | 0.05 | ohm
| V1 | new busbar voltage
| Ia1' | new current of machine 1
| Ia2' | currents of each of the other three machines
| RL | load resistance=240/800= |  |  | 0.3 | ohm
E1'-Ra*Ia1'=V1
E2-Ra*Ia2=V1
RL*(Ia1'+3*Ia2)=V1
Solve the three equations and obtain
| Ia1' |  |  |  | 352 | A | Answer
| Ia2 |  |  |  | 152 | A | Answer
| V1 |  |  |  | 242.4 | Volts
Assuming that 200 A is 100% full load current of each machine ,machine1 is loaded
more than 175% of its full load capacity. But the air circuit breaker of machine 1 will
trip immediately, and the other three machines will be called upon to supply the total
load. In short, there will be quite a chaotic condition for a short time in the station, which
at all costs must be prevented.
Back to top of page
Prob.1.8 | d.c motor- hysterisis & eddy current losses
A d. c motor running at 600 rpm has hysterisis loss of 360 W and eddy current loss of
120 W. Calculate the speed at which the total iron losses will be halved.
Solution: | f | frequency |  |  | k1,k2 are constants
| Wh | Hysterisis loss |  | =k1*f
| We | Eddy current loss |  | =K2*f*f
Since frequency is proportional to speed, N.,
| Wh |  |  | =K1*N
| We |  |  | =k2*N*N
| N |  |  | 600 | rpm
| Wh |  |  | 360 | W
| We |  |  | 120 | W
Therefore,
| k1 |  |  | 0.6
| k2 |  |  | 0.00033333
| N2 | speed at which total iron losses are halved
| Half of iron losses = |  |  | =(Wh+We)/2
|  |  |  | 240 | W
Therefore ,
k1*N2 + k2*N2*N2=( Wh+We)/2, a quadratic equation in N2.
Therefore,
N2=(-k1+sqrt(k1*k1+4*k2*((Wh+We)/2))/(2*k2)
|  |  |  | 336.9317 | rpm | Answer
Back to top of page
Prob.1.9 | d.c motor-efficiency
A motor is operated at no load from a 240 V supply and the input current is 4 A. If the
shunt field resistance is 240 ohms and the armature resistance is .32 ohm, calculate
(a) stray loss
(b) efficiency , when input current is 25 A.
Solution:
| V | supply voltage |  | 240 | Volts
| Rf | field resistance |  | 240 | ohms
| If | field current = V/Rf= |  | 1 | A
| I | Input current |  | 4 | A
| Ia | armature current |  | 3 | A
| Ra | armature resistance |  | 0.32 | ohm
| Eg |  |  | =V-Ia*Ra
|  |  |  | 239.04 | Volts
| W | stray loss |  | =Eg*Ia
| W |  |  | 717.12 | W | Answer
(b)
| I | Input current |  | 25 | A
| Ia | armature current |  | =I-If
|  |  |  | 24 | A
| Eg |  |  | =V-Ia*Ra
|  |  |  | 232.32 | Volts
| Pout |  |  | =Eg*Ia-W
|  |  |  | 4858.56 | W
Alternatively,
Pout=Pin-Ploss=V*I-Ia*Ia*Ra-If*If*Rf-W=4858.56W
| Pin |  |  | =V*I
|  |  |  | 6000 | W
| Efficiency |  |  | =Pout*100/Pin
|  |  |  | 80.976 | % | Answer
Back to top of page
Prob.1.10 | universal motor
A fractional kW series motor has a resistance of 20 ohms and an inductance of 1/ p
H. When connected to a 230 V D.C. supply and loaded to take 1 A it runs at 2000 rpm.
Determine the speed and power factor when connected to a 230 V ,50 Hz supply and
loaded to take the same current.
D.C.
| V | supply voltage |  | 230 | volts
| R |  |  | 20 | ohms
| I |  |  | 1 | A
| E | back emf | =V-R*I | 210 | volts
| N | speed |  | 2000 | rpm
On a.c of same value (r.m.s)
| L |  |  | 0.31831 | H
| f |  |  | 50 | Hz
| X | =2*3.14*f*L |  | 99.9491 | ohms
| I*X |  |  | 99.9491 | Volts
| I*R |  |  | 20 | Volts
Phasor diagram:
|  |  |  | IX | IR | +Er
|  |  | f |  | V
I
From phasor diagram, reactance drop leads current by 90 deg, IR drop and rotational
emf Er are in phase with the current(neglecting efffect of iron loss)
Hence
| Er |  |  | =sqrt(V*V-I*X*I*X)
|  |  |  | 207.1477 | Volts
For the same peak flux, the emf of rotation(rms) is 1/sqrt(2) of D.C. value; but peak flux
in a.c is sqrt(2) times flux on D.C. for same rms current, therefore Er is same for same
speed and is proportional to speed.
| hence new speed = |  |  | =Er*N/E
|  |  |  | 1972.8356 | rpm | Answer
| Pf | cos f | = | =(IR+Er)/V
|  |  |  | 0.9876 | lag | Answer
Back to top of page
Prob.1.11 | Field weakening
A d.c series motor having an overall resistance of 0.15 ohm has the following
characteristic at 600 V.
Current, A |  | 0 | 40 | 80 | 120 | 160 | 200
Speed, rpm |  | 3600 | 3600 | 2500 | 2100 | 1900 | 1780
If the field is weakened by tappings which reduce the number of turns/pole
to 70% of normal,at what speed the would the motor run when taking 160 A
from the 600V supply. Neglect armature reaction.
Solution:
The magnetisation characteristic(flux gainst current at constant speed) is
derived from the given torque/current curve as follows:
The emf can be calculated from the resistance and currents.
Since the flux is proportional to E/n, the pu flux (taking 200A as producing
1 pu flux) can be found from
Φpu =1.0(E/E200)(n200/n)
| current,I | Amps | 0 | 40 | 80 | 120 | 160 | 200
| IR drop, | V | 0 | 6 | 12 | 18 | 24 | 30
| E, | V | 0 | 594 | 588 | 582 | 576 | 570
| Φpu = |  | 0 | 0.51526 | 0.73448 | 0.86546 | 0.9467 | 1
·
AT 160 A, the flux is 0.95.The tappings reduce the effectiv ecurrent to 160*.7= 112 A.
The flux from the above graph at 112 A is about 0.84 pu.
The emf is not altered.
The new speed is = 1900*.95/.84= |  |  |  | 2148.8095 | rpm
The tapping changes the overall motor resistance ,but this is neglected.
·Explain why series motors are used in preference to shunt motors for traction applications.
·What would b ethe ffect of armature reaction?
Compare the use of diverter resistances and field tappings for series motor speed control.
Back to top of page
Prob.1.12 | D.C generator -Transient behaviour
The field winding of a separately excited d.c.generator has an inductance of 75 H
and a resistance of 150 ohms. The rotational mutual inductance coefficient
between the field and armature is 1 H/rad/s.
With the machine unexcited and driven at 1000 rpm , a ramp function voltage
v(t) =100t volts
is applied at t = 0 s to the terminals of the field winding. Determine the armature
emf at t= 0.5 s.
Solution:
The voltage equations for the field and armature circuits are:
vf =rf . If + Lf dif/dt=( rf+Lfp)uf
va =wr. Laf. if
vf =100t
Therefore, va = wr. Laf . 100t/(rf+Lf.p)
Transforming to s-domain for Laplace transforms,
va(s) = {100/[s.s(s+rf/Lf)]. }. (wrLaf/Lf)
| wr=1000x 2*3.1416/60 = |  |  |  | 104.72 | rad/s
| rf= |  |  |  | 150
| Lf= |  |  |  | 75
| alpha=rf/Lf= |  |  |  | 2
| Laf |  |  |  | 1
| beta=100 wr.Laf/Lf= |  |  |  | 139.6267
vas= beta/[s.s(s+alpha)]= beta[{(1/s.s))-1/(s(s+alph))}
vas= (1/(alph.alph){(alph/s.s)-alph/s(s+alph))
Coverting to time-domain,
va(t)= [beta/(alpha*alpha)](alpha.t -1+exp(-alpha.t)
| with t= |  |  |  | 0.5 | sec
| va(t)= |  |  |  | 12.8414
Back to top of page
Prob.1.13 | Fractional kW series motor
A fractional kW series motor has a resistance of 30 ohms and an inductance of
0.5 H. when connected to a 250 V d.c supply and loaded to take 0.8 A it runs
at 2000 rpm.Determine the speed and power factor when connected to a 250 V ,
50 Hz supply and loaded to take the same current.
Solution:
D.C.supply:
| I | A |  |  | 0.8
| r | ohms |  |  | 30
| Ir = |  |  |  | 24
| V= | volts |  |  | 250
| E=V-Ir | volts | Back-emf= |  | 226 | volts
A.C supply
| L | H |  |  | 0.5
| X=wL |  |  |  | 157.08
| IX= |  |  |  | 125.664 | volts
|  |  |  | Ir=24 V |  | Er
V= 250 V
IX=126 V
|  |  |  | Φ |  | I
Phasor diagram
Reactance drop leads currnt by 90 deg; Ir drop and rotational emf Er are
in phase with current ( effect of iron loss neglected)
| Er=sqrt(V*V-(IX)*(IX))-Ir= |  |  |  | 192.1216 | volts
For the same peak flux, the emf of rottaion(r.m.s) is 1/sqrt(2) of d.c value;
but peakflux on a.c is sqrt(2) times flux on d.c foer same r.m.s current.
Therefore,Er is same for same speed and is proportional to speed.
| Hence new speed =2000*Er/E |  |  |  | 1700.1914 | rpm
| p.f= ((Er+Ir)/ V) |  |  |  | 0.86449 | lag
Back to top of page
Prob. 1.14 |  | Speed controller of a d.c motor
A d. c motor is driving a loadd having an inertia of 200 kgm^2 and has its
speed controlled by a closed-loop system.Frictional torque= 10 Nm/rad/s and
the motor torque produced by the error signal is 100Nm per rad/s of error.
If the motor is at rest and the controller is suddenly set to demand a speed of 20
rad/s, develop an expression for the speed in terms of time and determine
the steady-state speed which will eventually reach.
Solution:
Equation of motion is:
Jd^2θo/dt^2 + F dθo/dt = K (dθi/dt - dθo/dt)
F= Frictional torque
θo= output
θi= demanded angular position
Hence,
d^2θo/dt^2 + (F+K dθo/dt )/Jdt = K dθi/dt
Changing to s- domain,
θo (s) .s^2 + (((F+k)/J)θo(s).s = (K/(s.J))dθi/dt
=(1/s) dθi/dt, is a sudden change of input in the form of a step function =20 rad/s
| (F+K)/J= |  |  |  | 0.55
| K/J= |  |  |  | 0.5
| (K/(s.J))dθi/dt= |  |  |  | 10
Therefore,
θo(s).S^2 +0.55 θo(s) .s = 10/s
θo(s)= 10/(s^2(s+0.55)= (10/0.55)[ (1/s^2) -(1/.55)(.55/(s+.55)]
Taking the inverse transform, we get
θo(t)= (10t/.55 ) -(10/.55^2 ) (1-exp(-.55t))
Hence speed= dθo/dt = (10/.55) -(10exp(-.55t)/.55^2)
Steady state speed (at t=¥)= 10/.55 = 18.2 rad.s
Back to top of page