## Sheet1
CHAPTER 12
Transient stability Problems
with Solutions
Prob. No: |  | Topic
12.1 |  | Equal area criterion of stability-Example1
12.2 |  | Equal area criterion of stability-Example2
12.3 |  | Inertia constant of two generators operating in parallel
12.4 |  | To determine the additional sudden load of an importing area without loss of
transient stability.
12.5 |  | To use the equal area criterion when the circuit breaker at one end of one
of two parallel lines opens suddenly.
12.6 |  | To predict the stability /instability of the system of Prob.12.5 when one of two
parallel lines opens at one end
12.7 |  | To predict the stability /instability of the system of Prob.12.5 when fault occurs
at the midpoint of one of two parallel lines.
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.12.1 | Equal area criterion of stability- Example 1
A generator delivers 1 pu power to an infinite busbar through a network. A fault occurs which
reduces the maximum power transferable to 0.4 pu whereas before the fault this power was
1.8 pu and after clearance of the fault 1.3 pu. Calculate the critical clearing angle , sketch
the power -angle curves and show the equality of the accelerating and decelerating areas.
Resistance may be neglected .
Solution: |  | P |  | Pm
P2
P0
P1
|  |  | d0 | d1 d2
| P0 |  |  | 1 | pu
| P1 |  |  | 0.4 | pu
| P2 |  |  | 1.3 | pu
| Pm |  |  | 1.8 | pu
| d0 | =asin(P0/Pm) |  | 0.58903 | radian
| d2 | =3.1416-Asin(P0/P2) |  | 2.5526 | radian
| Cos d1 | =(P0(d0-d2)+P1 *Cos (d0)-P2* Cos(d2))/(P1-P2)
0.61113
| d1 |  |  | 52.3286 | deg | Answer
Top of page
Prob.12.2 | Equal area criterion of stability-Example2
The transfer reactances between a generator and an infinite busbar operating at 132 kV ,
during and after a fault on the interconnector are:
| Before the occurrence of the fault |  |  |  | 140 | ohms per phase
| During the fault |  |  |  | 385 | ohms per phase
| After clearance of the fault |  |  |  | 175 | ohms per phase
If the fault is cleared after the generator rotor has advanced 80 electrical degrees from its
steady position before the fault , determine the maximum load aht could be carried without
the fault causing instability.
Solution:
|  | P |  | Pm
P2
P0
P1
|  |  | d0 | d1 d2
| Base MVA |  |  | 100
| Vb | base voltage |  | 132 | kV
| Ib | base current |  | 100/(1.73*132)
|  |  | = | 0.43791 | kA
| Zb | =Base kV*BasekV/Base MVA
|  |  |  | 174.24 | ohms
| Xb | reactance before |  | 0.80349 | pu
| Xd | reactance during |  | 2.2096 | pu
| Xa | reactance after |  | 1.0044 | pu
| P0 | Unknown
| P1 | =1/Xd |  | 0.45257 | pu
| P2 | =1/Xa |  | 0.99566 | pu
| Pm | =1/Xb |  | 1.2446 | pu
| d1 |  |  | 80 | deg
| Cos d1 |  |  | 0.17364
| Cos d1 | =(P0(d0-d2)+P1 *Cos (d0)-P2* Cos(d2))/(P1-P2)
=Po*(ASIN(Po/Pm)-(3.1416-ASIN(Po/P2)))+P1*COS(ASIN(Po/Pm))+P2*COS(ASIN(Po/P2))
In this equation ,Po is the only unknown .It is obtained by trial & error.Selecting a value
Po= .524 , we note that the R.H.S =.173645
Therefore P0= .524 pu or 52.4 MW is the solution.
Top of page
Prob.12.3 | Inertia constant of two generators operating in parallel
A generator A is rate at 50 Hz ,60 MW, 75 MVA, 1500 RPM , and has an inertia constant
H= 7.5 MJ/MVA. The corresponding data for another generator B is 50 Hz, 120 MW,133.3
MVA,3000RPM, 4.5 MJ/MVA
( I ) If these two generators operate in parallel in a power station, calculate H for the
equivalent generator on a base of 100 MVA
(ii) If the power station is connected to another power station which has two of each type
of generator , calculate H for the equivalent generator connected to an infinite busbar.
Solution: | (I)
| MVA base |  | Sbase | 100
| MVAa |  | Sa | 75
| MVAb |  | Sb | 133.3
| Ha |  |  | 7.5 | MJ/MVA
| Hb |  |  | 4.5 | MJ/MVA
| Equivalent H, |  | He =(HaSa+HbSb)/Sbase
|  |  |  | 11.6235 | MJ/MVA
(II)
| He1 for the first power station = |  |  | 11.6235 | MJ/MVA
He2 for the second power station=2*He1
|  |  |  | 23.247 | MJ/MVA
H for the equivalent generator connecte3d to an infinite busbar = He1*He2/(He1+He2)
|  |  |  | 7.749 | MJ/MVA | Answer
Top of page
Prob.12.4 | To determine the additional sudden load of an importing area without loss of
transient stability.
An importing power area has a total demand of 25 MW from an infinite busbar via an
interconnector. The steady-state power limit is 80 MW. Estimate using the equal -
area criterion the additional area load that could be suddenly switched on without the
system losing stability.
Solution:
Pm
|  |  | P1 |  |  |  | A2
|  | A1 | Po
|  |  |  | d0 d1 | d2
d1
Area A1=(d1- do)P1- Pm sin d dd
do
d2
Area A2= Pm sin d dd -(d2-d1)P1
d1
Equating the two areas we get
| P1= Pm (cos do -cosd2)/(d2-do) |  |  |  | or, Sind1= | (cos do -cosd2)/(d2-do)
| Po |  |  | 25 | MW
| Pm |  |  | 80 | MW
| do | = asin(Po/Pm) |  | 0.31782 | rad.
| cos do |  |  | 0.94992
| d2 | =3.1416-d1
| cos d2 | = |  | cos d1
| Therefore | Sind1= | (cos do -cosd2)/(d2-do)
=(cos do+cos d1)/(3.1416-d1-d0)
=(.949918+cos d1)/(2.82776-d1)
We will solve this equation by trial & error.
Let
| Try | d1= | 0.5 |  | LHS = | 0.47943 | RHS = | 0.78509
|  |  | 0.6 |  |  | 0.56464 |  | 0.79688
|  |  | 0.7 |  |  | 0.64422 |  | 0.8059
|  |  | 0.8 |  |  | 0.71736 |  | 0.81204
|  |  | 0.9 |  |  | 0.78333 |  | 0.81521
|  |  | 0.95 |  |  | 0.81342 |  | 0.81565
|  |  | 0.954 |  |  | 0.81574 |  | 0.81566
| d1= | .954 is the solution
Therefore
| P1= | = Pm sind1 |  | 65.2589 | MW | Answer
Top of page
Prob.12.5 | To use the equal area criterion when the circuit breaker at one end of one
of two parallel lines opens suddenly.
Consider the system shown below.
| Generator |  |  | X1 |  |  | Infinite bus
| Eg' | [6 empty] | E
|  |  | X2 |  | X3
| Xd' |  | B | F
| X1= | 0.4 | X2= | 0.2 | X3= | 0.2
|  | pu |  | pu |  | pu
| Xd' = | 0.2 | Eg'= | 1.2 | E= | 1
|  | pu |  | pu |  | pu
| Mechanical power input to generator = Pm = |  |  |  | 1.5 | pu
Suppose the system is operating in equilibrium at d1, when the breaker b inadvertently,
switching the operating point to the power angle curve Pe' below. Evaluate d1, d2 and d4.
Pe
2
[5 empty] | Pe' |  | A2
Pm=1.5
|  | A1 | 1
|  |  |  | d1 d2 | d3 d4
Solution: | At t=0-, total reactance between the two sources is Xd' + X where,
| X= |  |  | X1*(X2+X3)/X1+X2+X3
|  |  | = | 0.2 | pu
| Pe,max = |  |  | Eg'*E/(Xd'+X)
|  |  |  | 3 | pu
Pe' = Pm when d = d1
i.e. Pe,max Sind1= Pm , or
| d1= |  |  | Asin(Pm/Pe,max)
|  |  |  | 29.9999 | deg | Answer
At t=0 , B opens , and we have
| Pe',max = |  |  | Eg'*E/(Xd'+X1)
2
Pm = Pe'max Sin d2. Therefore,
| d2= |  |  | asin(Pm/Pe'max)
|  |  |  | 48.5903 | deg. | Answer
| d4= |  |  | 131.4097 | deg. | Answer
Top of page
Prob.12.6 | To predict the stability /instability of the system of Prob.12.5 when one of two
parallel lines opens at one end
Consider Prob.12.5 and predict whether thee system will be stable or unstable .If the
system is stable, evaluate d3
deg
Solution: | d1= | 30 | deg | d2= | 48.6 | deg | d4= | 131.4
|  | 0.5236 | rad |  | 0.84823 | rad |  | 2.2934
rad
In the interval d1 to d2 , Pm> Pe, and the rotor is accelerating
d2
| Area A1= |  |  | (Pm - Pe') d d
d1
d2
|  |  | = | (Pm- Pe'max Sind)d d
d1
|  |  | = | Pm( d2- d1) + Pe'max(cos d2 -Cos d1)
|  |  | = | 0.077519
The system will be stable when there is enough area A2 in the interval d2 < d < d4
to offset the acceleration.
d4
| A2max = |  |  | (-Pm + Pe') d d
d2
d4
|  |  | = | (-Pm + Pe'max Sind)d d
d2
|  |  | = | -Pm( d4- d2) - Pe'max(cos d4 -Cos d2)
|  |  | = | 0.47755
Since A2max > A1 , the rotor will not swing so far as d4 and the system is stable. The
rotor will stop when A2=A1. Therefore,
d3
(Pe'- Pm )dd = .0773
d2
or
d3
(Pe'max Sin d -Pm )dd = .0773
d2
which gives
-Pe'max (cos d3- cos d2) -Pm(d3-d2)=.0773
or,
1.5 d3 + 2 Cos d3 = 2.518
Use iterative method to solve this non-linear equation.
|  |  | d3= | d3= | d3= | d3= | d3= | d3=
|  |  | 1 | 1.1 | 1.2 | 1.21 | 1.22 | 1.218
| 1.5 d3 + 2 Cos d3= |  | 2.5806 | 2.5572 | 2.5247 | 2.521 | 2.5173 | 2.518
Therefore solution is :
|  | d3= | 1.218 rad
|  |  | 69.7861 | deg. |  | Answer
Top of page
Prob.12.7 | To predict the stability /instability of the system of Prob.12.5 when fault occurs
at the midpoint of one of two parallel lines.
Suppose a balanced three-phase fault occurs at F in the power system of Prob.12.5.
(a) If the fault is not removed , will the generator be stable?
(b) If the fault is cleared by opening the breaker B at dc = 60 deg; will the system be
stable?. If so, calculate d 3.
Solution: | (a) With the fault ,the system becomes
X1
Xd'
| Eg' |  | X2 | X3 |  | V
This can be reduced to :
X1
|  |  | Xd' | a
|  | Eg' |  | X2 | X3 |  | V
b
pu
| Eg'= | 1.2 | pu | Xd' = | 0.2 | pu | X1= | 0.4
| V= | 1 | pu | X2= | 0.2 | pu | X3= | 0.2
| The Thevenin equivalent of the circuit across a-b is: | [6 empty] | pu
|  |  | Xd' | a X4
|  | Eg' |  |  |  |  | Eth
b
|  | X4=X1*X2/(X1+X2)= |  | 0.13333 | pu
|  | Eth=V*X2/(X1+X2)= |  | 0.33333 | pu
Under faulted condition, Pe" = Pe"max Sind
Pe''max = Eg'Eth/(Xd'+X4)
|  |  |  | 1.2 | pu
Stability is impossible ,since Pe"max(=1.2) is less than Pm(=1.5),preventing even steady-state stability.
(b)
Pe
2
[5 empty] | Pe' |  | A2
Pm=1.5
|  | A1 | 1
Pe"
|  |  |  | d1 d2 | dc d3 d4
| Pemax = | Pre-fault |  | 3
| Pe'max = | Post-fault |  | 2
| Pe"max = | Faulted |  | 1.2
| If the fault is cleared at dc = |  |  | 60 | deg. | = | 1.0472 | rad.
| d1= | 30 | deg | Pm = | 1.5 | pu | d4=deg. | 131.4
|  | 0.5236 | rad |  |  |  | =rad | 2.2934
dc
A1= (Pm-Pe") dd= Pm(dc-d1)+ Pe"max(Cosdc-Cosd1)=
| d1 |  |  | 0.34617 | pu
Maximum available decelerating area is :
d4
A2max= (Pe'maxSind - Pm) dd = -Pe'max*(Cosd4-cosdc)-Pm (dc-dc)=
dc
|  |  |  | 0.45338 | pu
Since A2max > A1,system is stable.
To solve for d3,
d3
(Pe' - Pm)dd = A1
dc
or,
-Pe'max(cosd3-Cos dc)-Pm(d3-dc)=A1
or
1.5 d3+ 2*cosd3=-A1+Pe'maxCosdc=
2.225
or
1.5 d3+ 2*cosd3=2.225
This non-linear eq. Is solved below:
| d3= |  | 1 | 1.5 | 1.848 | radian
| 1.5d3+2*Cosd3= |  | 2.5806 | 2.3915 | 2.2247
The solution is :
| d3= |  |  |  | 1.848 | radian | Answer
Top of page