## Sheet1
CHAPTER 13
Overvoltage Problems
with Solutions
Prob.No. |  | Topics
13.1 |  | Surges in two transmission lines connected by an undergound cable
13.2 |  | Surges in a transmission line connected to an undergound cable through a
resistor
13.3 |  | Surges in a cable connected to an overhead line
13.4 |  | Surges in two transmission lines connected by an inductor
13.5 |  | Transient recovery voltage
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.13.1 | Surges in two transmission lines connected by an undergound cable
The ends of two long overhead lines A and B are connected by a cable C 1.5 km long.
The lines have capacitance 10 pF/m and inductance 1.6*10E-07 H/m and the cable has
capacitance 89 pF/ m and inductance 5* 10E-08. A rectangular voltage wave of magnitude
10 kV and of long duration, travels along line A towards the cable. Find the magnitude
of the second voltage step occurring at the junction of the cable and the lineB. What will be
the voltage at the junction of line A and the cable, 20 microsecond after the initial surge
reaches this point?
Solution: |  | Line A |  |  | Line B
|  | ZL |  |  | ZL | VT1
VT
Vr2
Cable C
Zc
VT2
| Ll | line inductance |  | 1.6e-06 | H/m
| Cl | line capacitance |  | 1e-11 | F/m
| LC | cable inductance |  | 5e-07 | H/m
| Cc | cable capacitance |  | 8.9e-11 | F/m
| Zl | line surge impedance = sqrt(Ll/Cl)
400
| Zc | cable surge impedance = sqrt(Lc/Cc)
|  |  |  | 74.9532 | ohms
| Kr1 | Reflection coefficient |  | =(Zc-Zl)/(Zc+Zl)
-0.68438
| Vi | Incident voltage |  | 10 | kV
| VT | Transmitted voltage into cable=(1+Kr1)*Vi
|  |  |  | 3.1562 | kV
| VT1 | Transmitted voltage into line B=2*Zl*VT/(Zc + Zl)
|  |  |  | 5.3163 | kV
| Vr2 | Reflected voltage from line B = (Zl - Zc)*VT/(Zl+Zc)
|  |  |  | 2.1601 | kV
| VT2 | Reflection of Vr2 at the junction of cable and line A=(Zl-Zc)*Vr2/(Zl+Zc)
|  |  |  | 1.4783 | kV
Lattice Diagram:
Vi=10
VT=3.15
VT1=5.3
Vr2=2.16
VT2=1.48
VT3=2.49
Vr3=1.01
| Vr3 | Second reflection from line B=Kr1*VT2=
|  |  |  | -1.0117 | kV
| Magnitude of Vr3 |  |  | 1.0117 | kV
| VT3 | Second transmitted voltage wave into line B=VT2+magnitude of Vr3=
|  |  |  | 2.49 | kV
Second voltage step at junction of cable & line B= VT!+VT3=
|  |  |  | 7.8063 | kV | Answer
| l | cable length |  | 1500 m
| cable travel time= |  |  | =lsqrt(lc*Cc)
| sqrt(lC*CC) |  |  | 6.6708e-09
| travel time |  |  | 1.0006e-05 | s
|  |  |  | 10 | microsec
Voltage at the junction of line A and cable, 20 microsec.after the initial surge reaches
| that point= |  |  | =VT+Vr2+VT2
|  |  |  | 6.7946 | kV | Answer
Top of page
Prob.13.2 | Surges in a transmission line connected to an undergound cable through a
resistor
An overhead line of surge impedance 400 ohms is connected to a cable of surge impedance
40 ohms through a series resistor. Determine the magnitude of the resistor such that it
absorbs maximum energy from a surge originating on the overhead line and travelling into
the cable. Calculate
(a) the voltage and current transients reflected back into the line.
(b) those transmitted into the cable in terms of the incident surge voltage of 1000kV, and
(c) the energies reflected back into the line and absorbed by the resistor.
Solution: |  | O/H line |  | Resistor | Cable
|  |  | A |  | B
|  | Z1 |  | R | Z2
vi
| Ii |  | vrA
IrA
Equivalent circuit:
Z1
A
R
|  |  | 2 vi |  | B
Z2
| vi |  |  | 1000 | kV
| Z1 |  |  | 400 | ohms
| Z2 |  |  | 40 | ohms
| vB |  |  | =2 *ViZ2/(Z1+Z2+R)
| vrA | =vB-vi |  | =(Z2+R-Z1)*vi/(Z1+Z2+R)
| IB | =2*vi/(Z1+Z2+R) |  | =2*Z1*Ii/(Z1+Z2+R)
| IrA |  |  | = Ii(Z1-Z2-R)/(Z1+Z2+R)
| Power absorbed by R |  |  | = RIi*Ii
=R(2Z1Ii/(Z1+Z2+R))*(2Z1Ii/(Z1+Z2+R))
It is maximum when d/dR(R/(Z1+Z2+R))=0, if Ii is given and constant.
This gives the condition that
| R |  |  | =Z1+Z2
|  |  |  | 440 | ohms
| vi |  |  | 1000 | kV
| IB | =2*vi/(Z1+Z2+R) |  | 2.2727 | kA | Answer
| Ii | =vi/Z1 |  | 2.5 | kA
| IrA |  |  | -0.22727 | kA | Answer
| vB |  |  | 90.9091 | kV | Answer
| vrA | =vB-vi |  | 90.9091 | kV | Answer
| Energy entering cable |  |  | =vBiB
|  |  |  | 206.6116 | MVA
| Energy absorbed by R |  |  | =R(Z1Ii/(Z1+Z2))*(Z1Ii/(Z1+Z2))
=Z1*Ii*Z1Ii/(Z1+Z2)
|  |  |  | 2272.7273 | MVA | Answer
| Energy incident |  |  | 2500
|  |  |  | 2500 | MVA
| Energy reflected |  |  | = Incident energy-Energy entering cable-energy absorbed
|  |  |  | 20.6612 | MVA | Answer
Top of page
Prob.13.3 | Surges in a cable connected to an overhead line
A cable of inductance .3 mH/phase and capacitance .4 microfarad per phase is connected
to a line of inductance 1.5 mH /ph and capacitance .012 microfarad /ph. All quantities are
per km. A surge of 1pu magnitude travels along the cable towards the line. Determine the
voltage set up at the junction of the line and the cable.
Solution: | Lc |  |  | 0.0003 | H
| Cc |  |  | 4e-07 | F
| Zc | = sqrt (Lc/Cc) |  | 27.3861 | ohms
| Ll |  |  | 0.0015 | H
| Cl |  |  | 1.2e-08 | F
| Zl | = SQRT(Ll/Cl) |  | 353.5534 | ohms
| K | Reflection coefficient |  | 0.85622
| Voltage at junction |  |  | =1+ k
|  |  |  | 1.8562 | pu | Answer
Top of page
Prob.13.4 | Surges in two transmission lines connected by an inductor
A rectangular surge of 2 microsecond duration and magnitude 2 pu travels along a line
of surge impedance 350 ohms. The latter is connected to another line of equal impedance
through an inductor of 800 microhenries. Calculate the value of the surge transmitted to
the second line.
Solution:
|  |  | Z | L | Z
|  |  |  | Z | I
2*vi
L
Z
Equivalent Circuit
| vi |  |  | 2 | pu
| Z |  |  | 350 | ohms
| L |  |  | 0.0008 | H
| t |  |  | 2e-06 | s
| I |  |  | =(2*vi/2*Z)*(1-exp(-2*Z*t/L))
| v in the second line |  |  | =I*Z
=vi*(1-exp(-2*Z*T/L))
|  |  |  | 1.6525 | pu | Answer
Top of page
Prob.13.5 | Transient Recovery Voltage
A 1-phase 50 Hz generator with one terminal earthed is excited to an internal emf of
10 kV and is connected to a system through a circuit breaker. The generator inductance
is 10 mH and the effective stray capacitance is represented by a 4 micro-Farad
capacitor across the circuit breaker. A short- circuit occurs beyond the circuit breaker.
Develop an expression for the voltage across the contacts immediately after the current
interruption if this occurs at an instant corresponding to 10 degrees prior to a natural
current zero.
| Solution: |  |  | L =10 mH
|  | 10 kV |  | C= 4 micro-F
Fig. Circuit diagram
|  | E=10 kV= |  |  | 10000 | V
|  | w= |  |  | 314 | rad/s
|  | L= |  |  | 0.01 | H
|  | C= |  |  | 4e-06 | F
|  | Short circuit current =E/wL = |  |  | 3184.7134 | A (r.m.s)
Rate of change at 10deg (assumed same as at zero) =sqrt(2)E/L= | [5 empty] | 1414213.5624 | A/s
value of current at 10deg=ic =2x3180x 0.123= |  |  |  |  | 782.28 | A
To bring the breaker current to zero , a current of i(t)= -ic +(sqrt(2) E/L. t
is imagined to be injected across the contacts.
The voltage necessary to inject this current into the circuit impedance
is the required transient voltage.
Transforming i(t) into s domain, we get:
i(s) = -ic/s + sqrt(2) E/Ls^2
v(s)= i(s). Z(s) = [-(ic/s) +sqrt(2)E/Ls^2] [ (Ls/Cs) /Ls+ 1/Cs)]
Let wo^2 = 1/LC. Then, after some algebra, we get
v(s) = -ic .sqrt(L/C). wo/(s^2 +wo^2) + 2Ewo^2/(L.s(s^2 +wo^2)
In time domain, the above equation becomes
v(t) = ic sqrt(L/C) sinwo.t +sqrt(2)E (1-coswot)
| wo= sqrt(1/LC)= |  |  |  | 5000
| sqrt(L/C)= |  |  |  | 50 | ohms
| ic sqrt(L/C)= |  |  |  | 39114
| sqrt(2)E= |  |  |  | 14142.1356
v(t) =- 39114 sin 5000t + 14142 (1-cos 5000t)
Top of page
E