## Sheet1
CHAPTER 14
Automatic Generation Control Problems
with Solutions
Topic | [7 empty] | Prob.No:
Governor charactreristics & load distribution | [7 empty] | 14.1
Power transfer & power frequency characteristics of two systems-Example 1 | [7 empty] | 14.2
Power transfer & power frequency characteristics of two systems-Example 2 | [7 empty] | 14.3
Frequency & tie-line power errors for a load change in a 2-area system | [7 empty] | 14.4
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.14.1 | Governor Characteristics & load distribution
Two 500 kW alternators run in parallel.The governors on the prime movers are so set that
the frequency drops from 51 Hz to 49 Hz from no load to full load in one, while in the other
from 51 to 49.5 Hz . Calculate
(a) the load on each machine when the total load is 750 kW, and
(b) the frequency at this load
Solution:
| 51 | Q |  | 500 kW |  | 51
P
| 50.5 |  |  |  |  | 50.5
frequency
| 50 |  |  |  |  | 50
R
| 49.5 | M |  |  | N | 49.5
|  | X' | P' |  | Y' |  | h
| 49 |  |  |  |  | 49
|  |  | 500 kW |  | Y
750 kW
Load
The intersection point R of the two load lines gives the loads on the two machines.
MR=(MQ/XQ)XQ'=(1.5-h)*500/2
Triangles NPR and Y'PP' are similar.
NR = NP (Y'P'/Y'P) = (1.5-h) *500/1.5
MR+NR= 750= (1.5-h)*((500/2)+(500/1.5))
h= 1.5 - 750/(250+333.3)= .214
| MR= (1.5-h)*500/2=321.5 kW |  |  |  | Answer
| NR= 750-321.5=428.5 kW |  |  |  | Answer
| Frequency= 49.5+.214= 49.714 |  |  |  | Answer
Back to top of page
Prob.14.2 | Power transfer & power frequency characteristics of two systems
A power system A has apower frequency characteristic such that a drop in frequency of
0.1 Hz is caused by an additional load of 250 MW, and the corresponding load change on
adjacent network B for the same fequency deviation is 400 MW. At a certain time A is
running at 49.85 Hz and B at 50 Hz. What would be the power transfer if the two systems
were to be paralleled via short ac interconnector?
Solution: |  | Ka,fa |  |  | Kb. fb
Ptie
| System |  |  |  |  | System
| A |  |  |  |  | B
Load frequency characteristics:
| Ka |  |  | 250 | MW/0.1 HZ
| Ka |  |  | 2500 | MW/Hz
| Kb |  |  | 400 | MW/0.1 HZ
| Kb |  |  | 4000 | MW/Hz
Frequencies:
| fa |  |  | 49.85 | Hz
| fb |  |  | 50 | Hz
| Ptie | Tie line flow= Ka*Kb*(fa-fb)/(Ka+Kb)
|  |  |  | -230.7692 | MW from B to A |  | Answer
Back to top of page
Prob.14.3 | Power transfer & power frequency characteristics of two systems-Example 2
Two power systems A and B are interconnected by a tie line and have power-frequency
constants KA and KB, MW/Hz. An increase in load of 500 MW on system A causes a
power transfer of 300 MW from B to A. When the line is open , the frequency of system A
is 49 Hz and of system B is 50 Hz. Determine KA and KB.
Solution: |  | A |  | B
dPt
|  | KA |  |  | KB
Change in frequency in A due to extra load dP and extra input dPt from B
=-(dP - dPt)/KA
Drop in frequency in B due to extra load = -dPt/KB
the two changes in frequency, we get
| dPt |  |  | = KB*dP/(KA+KB) |  | …….Eq.1
Now open the link:
|  | KA |  |  |  | KB
|  | fA |  |  |  | fB
|  |  | A |  | B
B is relieved of dPt and assumes fB
A has dPt more load and assumes fA.
fB = f + dPt/KB
| fA = f-dPt/KA |  |  |  |  | …Eq.A
Therefore,
| dPt=(fB - fA)*KB*KA/(KA+KB) |  |  |  |  | ….Eq.2
Eliminating KB/(KA+KB) from eqs.1&2, we get
| KA | = dP/(fB-fA) |  |  |  | …Eq.3
| dP |  |  | 500 | MW
| fB |  |  | 50 | Hz
| fA |  |  | 49 | Hz
Therefore,
| KA |  |  | 500 | MW/Hz | Answer
| dPt |  |  | 300 | MW
From Eq.2 we get
| KB | = KA dPt/(dP - dPt)
|  |  |  | 750 | MW/Hz | Answer
Back to top of page
Prob.14.4 | Frequency & tie-line power errors for a load change in a 2-area system
Two power systems A and B , each have regulation (R) of .1 pu (on respective capacity
bases) and a stiffness K of 1 pu. The capacity of system A is 150 MW and of B is 100 MW.
The two systems are interconnected through a tie line and are initially at 50 Hz.
If there is a 10 MW load change in system A, calculate the change in the steady-state
values of frequency and power transfer
Solution: | PA |  |  | 150 | MW
| PB |  |  | 100 | MW
| KA |  |  | 150 | MW/Hz
| KB |  |  | 100 | MW/Hz
| RA = RB = |  |  | 0.1 | pu
| f |  |  | 50 | Hz
| RA, Hz/MW |  | =change in frequency-no Load to full Load/full Load capacity
|  |  | = | =RA(pu)*f/PA |  | Hz/MW
|  |  |  | 0.033333 | Hz/MW
| RB, Hz/MW |  | = | =RB(pu)*f/PB |  | Hz/MW
|  |  |  | 0.05 | Hz/MW
| Change in load |  |  | 10 | MW
| Steady-state error in frequency = |  |  | =-change in Load/(KA +(1/RA)) +(KB +(1/RB))
|  |  |  | -0.033333 | Hz | Answer
| Steady-state error in tie-line flow |  |  | =-change in load*(KB + (1/RB))/(KA+(1/RA)+KB +(1/RB))
|  |  |  | -4 | MW | Answer
Back to top of page