## Sheet1
CHAPTER 15
Voltage & Reactive Power Control Problems
with Solutions
Prob. No: | Topic
15.1 | Cost of power factor improvement
15.2 | Reactive power required to re-establish the fall in voltage due to load.
15.3 | Load angle for a given load across an interconnector with the ends maintained at different
voltages
15.4 | Two generating stations connected by an interconnector- voltage adjustments required to
equalise the loads at the two stations
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.15.1 | Cost of power factor improvement
A consumer's load of 250 kw has power factor of 0.78 lagging. The power supply charges
are 50 cents per kVa of maximum demand per month plus 0.5 cents per kW -hr. The cost
of power factor improving apparatus is US dollar 10 per kVA, and the rate of interest
& depreciation is 10 %. To what extent the power factor should be improved so that the
amount saved is a maximum?. Calculate also the kVA capacity of the power factor
improving apparatus.
Solution:
|  | O |  | P kW |  | A
f1
f2
New kVA
| Old kVA |  |  |  |  | C
kVAr capacity of power factor
improving apparatus
B
| pf1 | cos f1 |  | 0.78 | lag
| pf2 | most economical pf, |  | cos f 2
| P |  |  | 250 | kW
kVAr capacity of power factor improving apparatus
=P * (tan f1- tan f2)
| U | cost of power supply |  | 0.5 | USD/kVa
| E | cost of energy |  | 0.05 | USD/kW-hr
| A | cost of apparatus |  | 10 | USD
| I | Interest & depreciation |  | 10 | %
| B | Annual charge for power factor improving apparatus = A*(I/100)*P*(tan f1 -tan f2 )
| D | Saving by improving the pf is = U*((P/ pf1)-(P/pf2))= Consumer's gross saving
| S | Consumer's net saving = D-B
To maximize S,
(dS/d f2) =0= (dD/d f2 )-(dB/d f 2) =-U*Ptan (f 2) * sec( f2)+ A*(I/100)*Psec f2*sec f2
| or sin f2 = A*(1/100)/U |  |  | 0.2
| Cos f2 |  |  | 0.9798 | lag |  | Answer
Capacity of power factor improving apparatus
=P * (tan f1- tan f2)
|  |  |  | 127.6231 | kVAr |  | Answer
Top of Page
Prob.15.2 | Reactive power required to re-establish the fall in voltage due to load.
Three supply points A,B and C are connected to a common busbar M. Supply point A
is maintain at a nominal 66 kV and is connected to M through a 66/33 kV transformer
(0.1 pu reactance) an a 33 kV line of reactance 20 ohms. Supply point B is nominally at
33 kV and is connected to M by a 66/33kV transformer (0.1 pu reactance0 and a 33 kV
line of 20 ohms reactance.
If at a particular system load , the line voltage at M falls by 5 kV, calculate the magnitude
of the reactive volt-ampere injection required at M to re-establish the original voltage.
The pu values a re based on a 100 MVA base.
Solution: |  |  | .1 pu | 20 ohms | M
|  | A |  |  |  | B
|  |  | 66/33 kV |  | 20 ohms
|  | 66 kV |  | 20 ohms |  | 33 kV
|  |  |  | .1pu | 66/33 kV
|  |  |  | 66 kV | C
| MVAb |  |  | 100
| Xb | in 33 kV circuit |  | 10.89 | ohms
| Xl | Line reactance |  | 20 | ohms
| Xlpu |  |  | 1.8365 | pu
|  |  | j.1 | j1.836 | j1.836
|  | A |  |  | M | B
j1.836
j.1
C
N
| Xt | Transformer reactance |  | 0.1 | pu
| Xa | Reactance M to A |  | 1.9365 | pu
| Xd | Reactance M to C |  | 1.9365 | pu
| Parallel combination of Xa & Xd |  |  | 0.96827 | pu
| Xc | Reactance M to B |  | 1.8365 | pu
| Equivalent reactance M to N |  |  | 0.63401 | pu
Fault MVA at M = MVAb/equivalent reactance=
|  |  |  | 157.7266 | MVA
Fault current = Fault MVA*1000/(1.73205*33)=
|  |  |  | 2759.501 | A | at 0 power factor lagging
d Qm/ d Vm =1.73205*fault current=
|  |  |  | 4779.5936 | Vars/Volt
|  |  |  | 4.7796 | MVAr /kV
| Drop in voltage at M(l-L) |  |  | 5 | kV
| Reactive power required |  |  | 23.898 | MVAr | Answer
Top of Page
Prob.15.3 | Load angle for a given load across an interconnector with the ends maintained
at different voltages
Two units of generators maintain 66 kV (L-L) and 60 kV (L-L) at the ends of an
interconnection of inductive reactance per phase of 23.094 ohms and with negligible
resistance and shunt capacitance. A load of 12 MW is to be transferred from the 66 kV
unit to the other end.
Calculate the load angle across the interconnector, and the power factor of the current
transmitted.
Solution: |  |  |  | I
jX
|  | Vs d |  | Vr
| I | = Vs d - Vr o |  | = Vs Cos d + jVs Sind -Vr
|  | jX |  |  | j X
| S | Complex power |  | = Vr *I conjugate
= VrVs Sin d -jVr (Vr-Vs Cosd )
X
| P | Real power |  | Vr.VsSin d/X
| P |  |  | 12 | MW
| Vs |  |  | 66 | kV
| Vr |  |  | 60 | kV
| X |  |  | 23.04 | ohms
| Sin d |  |  | =PX/Vr*Vs
0.069818
| d |  |  | 4.0035 | deg | Answer
| Cos d |  |  | 0.99756
| tan f |  |  | =(-Vs cos d+ Vr)/Vs Sin d
-1.2678
| cos f |  |  | 0.61931 | lag | Answer
Top of Page
Prob.15.4 | Two generating stations connected by an interconnector- voltage adjustments
required to equalize the loads at the two stations
Two generating stations A and B are linked by a line and two transformers of total
20 ohms referred to 132 kV and negligible resistance. A load of 100 MW .9 pf lagging is
by the busbars of A and 200 MW ,.85 pf lagging from B. Determine the phase angles
between the busbars of A and b, and the voltage adjustment required to equalize the load
on each station. Initially both stations have busbar voltages of 11 kV which are in phase
Solution: |  | PA |  |  | P, Q, I |  | PB
| A | [6 empty] | B
|  |  |  | X= | 20 ohms
|  |  | VA |  |  | VB
|  | P1=100 MW,.9 pf |  |  |  |  | P2=200MW, .85 pf
Phasor diagram:
VA
dV
|  |  | d |  | jX.I
VB
I
DV
| P1 |  |  | 100 | MW
| pf1 |  |  | 0.9 | lag
| Q1 | =P1*tan (ACOS(pf1)) |  | 48.4322 | MVAr
| P2 |  |  | 200 | MW
| pf2 |  |  | 0.85 | lag
| Q2 | =P2*tan (ACOS(pf2)) |  | 123.9489 | MVAr
To equalize the load on each station,
| PA = PB = |  |  | 150 | MW
| P | =PA-P1 |  | 50 | MW
| QA = QB = | =(Q1+Q2)/2 |  | 86.1905 | MVAr
| Q | =QA-Q1 |  | 37.7583 | MVAr | ,ignoring Qloss = I*IX in line
From the phasor diagram,
| dV |  |  | =X*Pph/VB
| X |  |  | 20 | ohms
| VB | per phase |  | 76.2103 | kV
| Pph | per phase |  | 16.6667 | MW
| dV |  |  | 4.3739 | kV
From the phasor diagram,
| Sin d | =dV/VA=dV/VB= |  | 0.057392
| d |  |  | 3.2918 | deg | Answer
Hence busbar A is 3.29 deg in advance of busbar B.
| DV | = XQph/VAph
| Qph |  |  | 12.5861 | MVAr
| VA | per phase |  | 76.2103 | kV
| DV | = XQph/VAph |  | 3.303 | kV per ph
|  |  |  | 5.721 | kV(L-L) | Answer
5.75 kV increase on 132 side of A
Top of Page