## Sheet1
CHAPTER 16
Economic Operation Problems | [6 empty] | e.mail address: Indulkar@ieee.org
with Solutions
Prob. No: |  | Topic
16.1 |  | Load sharing of two generating units -given the incremental fuel costs
16.2 |  | Penalty factors of plant
16.3 |  | Load sharing of two units considering penalty factors
16.4 |  | Saving in operating costs for economic load sharing compared to equal load
sharing between two units
16.5 |  | Load sharing of two generating units -given the variable operating costs
16.6 | Load sharing of two generating units -given the variable operating costs-considering losses
16.7 |  | Economic choice of plant
Chapters
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.16.1 | Load sharing of two generating units -given the incremental fuel costs
The incremental fuel costs (in $ per MW-hr ) for two generating units are given by
dc1/dPG1 = .008 PG1 + 8
dc2/dPG2 = .009 PG1 +6
Determine how a load of 1000 MW should be shared by the two generating units for
minimum fuel cost.
Solution: | Equate the incremental fuel costs;
| .008 Pg1 + 8 = .009 Pg2 + 6 |  |  |  |  | Eq.1
| Pg1 + Pg2 = 1000 |  |  |  |  | Eq.2
Solving these two equations we get:
-1
| Pg1 | = | .008, -.009 | '-2
| Pg2 |  | 1, 1 | 1000
Let
| A |  | 0.008
| B |  | -0.009
| C |  | 1
| D |  | 1
| AD-BC |  | 0.017
| Pg1 | = | 58.8235 | 0.52941 | -2
| Pg2 |  | -58.8235 | 0.47059 | 1000
|  | = | 411.7647 | MW | Answer
|  |  | 588.2353 | MW | Answer
Top of Page
Prob.16.2 | Penalty factors of plant
In a 2-plant system , the entire load is located at plant 2,which is connected to plant 1 by a
transmission line. Plant 1 supplies 100 MW of power with a corresponding transmission
of 5 MW. Calculate the penalty factors for the two plants.
Solution: | Since all load is at Plant 2, varying P2 does not affect the transmission loss ,Ploss. Thus
from Ploss =P1*P1*B11 + 2*P1*P2*B12 + P2*p2*B22, we get
Ploss = P1*P1*B11 or
| B11 | = P1*P1/Ploss
| Ploss |  |  | 5 | MW
| P1 |  |  | 100 | MW
| B11 |  |  | 0.0005 | (1/MW)
| dPloss/dP1 |  |  | =2*P1*B11
0.1
| Penalty factor for the first unit,L1 |  |  | =1/(1-dPloss/dP1)
|  |  |  | 1.1111 |  | Answer
| dPloss/dP2 |  |  | 0
| Penalty factor for the second unit,L2 |  |  | =1/(1-dPloss/dP1)
|  |  |  | 1 |  | Answer
Top of Page
Prob.16.3 | Load sharing of two units considering penalty factors
For the system of Prob.16.2, l = $15/MWh, and the incremental fuel costs for the two plants
are given by
| dF1/dP1 = .01 P1 +10 |  |  | ($/MW hr)
| dF2/dP2 = .02 P2 + 12 |  |  | ($/MW hr)
How much power should be generated at each plant for minimum total fuel cost?
Solution: | The penalty factors from Prob.16.2 are :
| L1 |  |  | 1.111
| L2 |  |  | 1
| l |  |  | 15 | $/MWhr
dF1/dP1= l *L1
or, | (.01P1+10)*L1=l
or, | P1 | =(( l /L1)-10)/.01 |  | 350.135 | MW | Answer
Similarly,
dF2/dP2= l *L2
or, | (.02P2+12)*L1=l
or, | P2 | =(( l /L2)-12)/.02 |  | 150 | MW | Answer
Top of Page
Prob.16.4 | Saving in operating costs for economic load sharing compared to equal load
sharing between two units
Incremental fuel costs for two generating units in a plant are given by
dF1/dP1 = .02 P1 +4 ($/MW-hr)
dF2/dP2 = .024 P2 +3.2 ($/MW -hr)
Total load varies from 50 to 25 MW.
Maximum and minimum loads on each unit are to be 125 and 20 MW respectively.
Determine the saving in fuel cost in $ /hour for economic distribution of a total load of 180
MW , compared with equal distribution.
Solution: | Equating incremental costs, we get
| .02 P1-.024 P2 =-.8 |  |  |  | Eq.1
| P1 + P2= |  | 180 |  | Eq.2
Rewrite:
| .02 P1-.024 P2 = |  | -0.8
| .024P1+.024P2= |  | 4.32
Add:
| 0.044 | *P1= | 3.52
| P1 |  | 80 | MW | Answer
| P2 |  | 100 | MW | Answer
Increase in cost for Unit 1:
90
|  | (.02P1 +4)dP1= |  | .02*90*90/2+4*90-.02*80*80/2-4*80
|  |  | = | 57 | $/hr
80
for Unit 2:
90
|  | (.024 P2 +3.2)*dP2= |  | (.024*90*90/2)+3.2*90-(.024*100*100/2+3.2*100)
| 100 |  |  | -54.8 | $/hr | Decrease in cost
| Net increase in cost= |  |  | 2.2 | $/hr | Answer
Top of Page
Prob.16.5 | Load sharing of two generating units -given the variable operating costs
The variable operating costs of two generating units are given by
| C1= 10P1 +.008P1*P1 |  |  |  | $/hr
| C2= 8P2+ .009P2*P2 |  |  |  | $/hr
If the total load demand varies from 120 to 140 MW ,determine the power output of each
unit(coal-fired), the incremental operation cost, and the total operating cost CT that minimizes
CT for the load demands, 120,130, and 140 MW.
Solution: | For minimum cost,dC1/dP1=dC2/dP2,
dC1/dP1= a+bP1,and
dC2/dP2= c+d*P2,where
| a | = |  | 10 | 10 | 10
| b | = |  | 0.016 | 0.016 | 0.016
| c | = |  | 8 | 8 | 8
| d | = |  | 0.018 | 0.018 | 0.018
| PT | total load ,MW |  | 120 | 130 | 140 | MW
minimum cost,a+bP1=c+dP2…….eq.1
P2=PT-P1…………………………..eq.2
Using (2) in (1),
| P1=(d*PT+c-a)/(b+d) |  |  | 4.7059 | 10 | 15.2941 | MW | Answer
| P2=PT-P1 |  |  | 115.2941 | 120 | 124.7059 | MW | Answer
Incremental cost when CT is minimized is
dC2/dP2=dC1/dP1=a+bP1=
|  |  |  | 10.0753 | 10.16 | 10.2447 | $/MWh | Answer
Minimum total operating cost is CT=C1+C2=aP1+bP1*P1+cP2+dP2*P2
|  |  |  | 1209.0353 | 1320.8 | 1434.2588 | $/h | Answer
Top of Page
Prob.16.6 | Load sharing of two generating units -given the variable operating costs-considering losses
-g losses
Total transmission loss for the power system of Prob.16.5 is given by
PL = .00015P1*P1 +.00002P1*P2 +.00003P2*P2 (MW)
P1,P2 are in MW
Determine the output of each unit, total transmission loss, total load, total cost,
when the area l =10.1 $/MWh
Solution: | Let PL =eP1+fP1*P2+gP2*P2,where
| e | = |  | 0.00015
| f | = |  | 2e-05
| g | = |  | 3e-05
| l |  |  | 10.1 | $/MWh
l =dC1/dP1=(dC1/dP1)*(1/(1-dPL/dP1))=(a+bP1)/(1+2eP1-fP2)
l =dC2/dP2=(dC2/dP2)*(1/(1-dPL/dP2))=(c+dP2)/(1+2gP2-fP1)
Rearranging the above two equations:
| AP1+BP2=X |  |  |  |  | eq.1
| CP1+DP2=Y, where |  |  |  |  | eq.2
| A | =b+2el |  | 0.01903
| B | = fl |  | 0.000202
| C | =fl |  | 0.000202
| D | =d+2gl |  | 0.018606
| X | l-a |  | 0.1
| Y | l-c |  | 2.1
Solving eqs.1 &2, we get
| P1=(DX-BY)/(AD-BC) |  |  | 4.0573 | MW | Answer
| P2=(-CX+AY)/(AD-BC) |  |  | 112.8228 | MW | Answer
| Loss, PL= | e*P1*P1+f*P1*P2+g*P2*P2=
|  |  |  | 0.39349 | MW | Answer
| PT=P1+P2-PL= |  |  | 116.4865 | MW | Answer
CT=C1+C2=aP1+bP1*P1+cP2+d*P2*P2=
|  |  |  | 1187.6623 | $/h | Answer
Top of Page
Prob. 16.7 | Economic choice of plant
A load of 75 kW is to be supplied for 2500 h/year by a motor and the overall
power factor must be not less than 0.9. A new induction motor of efficiency
92% and power factor 0.9 and a second -hand motor of efficiency 91%
and power factor 0.83 are available. Lossless capacitors costing IR 700 per
kVA can be used to raise the power factor of the second-hand motor to 0.9.
All interest and depreciation charges may be taken as 12% per year and the
tariff for energy is IR 600 per kVA of maximum demand plus IR 45 per kWh.
By how much should the price of the second-hand motor be less than that
of the new motor in order to make its use economical.
Solution:
New motor:
| Output= |  |  | 75 | kW
| Efficiency= |  |  | 0.92
| Input= | output/efficiency= |  | 81.5217 | kW
| Loss= Input-Output= |  |  | 6.5217 | kW
| Cost per kWh |  |  | 45 | IR
| Hours |  |  | 2500
Cost of loss= Loss* hours* cost per Wh=
7336.9565
| power factor= |  |  | 0.9
Maximum demand=output/(efficiency*power factor)
|  |  |  | 90.5797 | kVA
| Tariff for energy |  |  | 600 | IR
| cost = |  |  | 54347.8261
| Total yearly cost = |  |  | 61684.7826 | IR
Second-hand motor:
| Output= |  |  | 75 | kW
| Efficiency= |  |  | 0.91
| Input= |  |  | 82.4176 | kW
| Loss= Input-Output= |  |  | 7.4176 | kW
| Cost per kWh |  |  | 45 | IR
| Hours |  |  | 2500
Cost of loss= Loss* hours* cost per Wh=
|  |  |  | 8344.7802 | IR
| Raised power factor= |  |  | 0.9
Maximum demand=output/(efficiency*power factor)
|  |  |  | 91.5751 | kVA(with capacitors)
| Tariff for energy |  |  | 600 | IR
| cost = |  |  | 54945.0549 | IR
| original pf of second-hand motor= |  |  | 0.83
Rating of capacitors= Output(tancosinverse(original pf)- tan Cosinverse(raised pf))
|  |  |  | 14.0761 | kVAr
| capacitor cost |  |  | 700 | per kVA
| Cost= |  |  | 9853.304 | IR
| Interest & depreciation 12% |  |  | 0.12
| yearly cost= |  |  | 1182.3965 | IR
| Total yearly cost = |  |  | 64472.2316 | IR
| Yearly difference= |  |  | 2787.449 | IR
Difference in cost of second-hand motor=yearly difference/Interest & depreciation
|  |  |  | 23228.7419 | IR
Top of Page