## Sheet1
CHAPTER2
Synchronous machine problems
with Solutions
Sub-topics |  |  |  |  | Problems
Synchronous generator-Winding distribution factor |  |  |  |  | 2.1
Synchronous generator-Induced voltage & distribution factor |  |  |  |  | 2.2
Synchronous generator-Breadth factor and coil pitch factor |  |  |  |  | 2.3
Synchronous generator- with unity pf load-Phasor diagram |  |  |  |  | 2.4
Synchronous generator-Parallel operation-Example 1 |  |  |  |  | 2.5
Synchronous generator -Parallel operation-Example 2 |  |  |  |  | 2.6
Synchronous motor-Power factor improvement |  |  |  |  | 2.7
Synchronous motor-excitation voltage & torque |  |  |  |  | 2.8
Synchronous motor-Operation |  |  |  |  | 2.9
Synchronous motor- operation in parallel with a resistive load |  |  |  |  | 2.1
Synchronous motor-induced emf & mechanical power developed |  |  |  |  | 2.11
Synchronous motor -maximum torque |  |  |  |  | 2.12
Synchronous generator-Performance Chart |  |  |  |  | 2.13
CONTENTS |  |  |  |  | CHAPTER0
Synchronous motor- Induced emf |  |  |  |  | 2.14
Synchronous motor-salient-pole-maximum power |  |  |  |  | 2.15
Synchronous machine-operation at maximum power |  |  |  |  | 2.16
Synchronous generator connected to infinite bus-Effect of changing
Excitation |  |  |  |  | 2.17
Synchronous motor- for power factor improvement |  |  |  |  | 2.18
Synchronous generator-Regulation from Magnetization curve |  |  |  |  | 2.19
Synchronous motor-Current & Power factor |  |  |  |  | 2.2
Synchronous generator -Salient pole-performance |  |  |  |  | 2.21
Synchronous generator -Parallel operation-Example3 |  |  |  |  | 2.22
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.2.1 | Synchronous generator-Winding distribution factor
Calculate the value of the distribution factor for a 3-phase alternator having 12-slots per
pole.
Solution: | slots/pole = |  | 12
a, Electrical angle(radians) between adjacent slots =(180/12)*(3.1416/180)=
0.2618
| m, slots/pole/phase = |  | 4
Kd, distribution factor = Sin(ma/2)/m.sin(a/2)=
|  |  | 0.95766 |  | Answer
Back to top of page
Prob. 2.2 | Synchronous generator-Induced voltage & distribution factor
A 3-phase 4-pole alternator has a winding with 8 conductors per slot. The armature has
a total of 36 slots. Calculate the distribution factor . What is the induced voltage per phase
when the alternator is driven at 1800 RPM, with flux of 0.041 Wb in each pole?
Solution:
| f, flux per pole |  | 0.041 | Webers
Z, No. of conductors /phase=36*8/3=
96
| N, speed, rpm |  | 1800
| P, No. of poles |  | 4
| f,frquency=NP/120 |  | 60
| slots/pole |  | 9
| a=P/9 |  | 0.34907
| slots/pole/phase,m |  | 3
| Kd |  | 0.95979
| V=2.22 f Z(F) (Kd)= |  | 503.1967 | Volts/phase |  | Answer
Back to top of page
Prob.2.3 | Synchronous generator-Breadth factor and coil pitch factor
A 10 MVA ,11 KV,50 Hz ,3-phase star-connected alternator s driven at
300 RPM. The winding is housed in 360 slots and has 6 conductors per
slot, the coils spanning (5/6) ths of a pole pitch. Calculate the sinusoidally distributed
flux per pole required to give a line voltage of 11 kV on open circuit, and the full-load
current per conductor.
Solution: | f, frequency |  | 50 | Hz
| N, speed, RPM = |  | 300
P= No. of poles =120f/N
20
| slots/pole=360/20= |  | 18
a, Electrical angle(radians) between adjacent slots =(180/18)*(3.1416/180)=
0.17453
| m, slots/pole/phase = |  | 6
Kd, distribution factor = Sin(ma/2)/mSin(a/2)=
0.95614
Pitch factor, Kp = cos (b/2)
| b=3.1416-(5/6)*3.1416= |  | 0.5236 | radians
| Kp = |  | 0.96593
E=2.22 f.Z.F. Kd. Kp
E = emf per phase=11000/1.73205
|  |  | 6350.8559 | Volts
Z, conductors per phase =
720
F, flux per pole=E/2.22 f. Z. Kd. Kp =
|  |  | 0.086042 | Webers | Answer
I=10*10E05/(1.73205*11000)
|  |  | 524.8641 | Amps. | Answer
Back to top of page
Prob.2.4 | Synchronous generator- with unity pf load-Phasor diagram
A 3-phase star-connect4ed 50 Hz alternator has 96 conductors per phase, and a flux
per pole 0f 0.1 Wb. The alternator winding has a synchronous reactance of 5 ohms
per phase and negligible resistance. The distribution factor for the stator winding is
0.96.Calculate the terminal voltage when three non-inductive resistors of 10 ohms per
phase are connected in star across the terminals. Sketch the phasor diagram .
Solution: |  | Phasor Diagram
E
jIX
|  |  |  | I | V
E = emf per phase
| Kd, distribution factor |  | 0.96
Z, conductors per phase =
96
| F, flux per pole = |  | 0.1 | Wb
| f, frequency |  | 50 | Hz
| E=2.22 f. Z. F. Kd |  | 1022.976 | Volts
X, Synchronous reactance =
|  |  | 5 | ohms
V = SQRT(E*E - I*I*X*X)
Load current I = V/load resistance=V/10
Therefore, V = E/sqrt(1+(X*X/10*10))
|  |  | 914.9776 | Volts/phase
| V(L-L) |  | 1584.7869 | Volts | Answer
Back to top of page
Prob.2.5 | Synchronous generator-Parallel operation-Example 1
Two single-phase generators are connected in parallel, and the excitation of each
machine is such as to generate an open-circuit emf of 3500 V. The stator winding of
machine has synchronous reactance of 30 ohms and negligible resistance. If there is
a phase displacement of 40 electrical degrees between the emf's ,calculate:
(a) the current circulating between the two machines,
(b) the terminal voltage, and
(c) the power supplied (kW) from one machine to the other.
Assume that there is no external load. Sketch the phasor diagram.
Solution: | Circuit diagram:
|  |  | j30 ohms | j30 ohms
| E1=3500 | 0 deg. | V |  |  | E2=3500 | -40 deg.
Phasor diagram:
E1
V
I
E2
| I=(E1-E2)/j60 |  | =(3500 | 0- 3500 | -40)/j60
Im I=(-3500+3500Cos(40*3.14/180))/60=
-13.6341
RE I=3500*Sin(40*3.14/180)/60
37.4801
I = sqrt(reI*reI + ImI*ImI)=
|  |  | 39.8829 | Amps | Answer
V=3500-j30*(ReI + jImI)
| Re V=3500+30*Im I= |  | 3090.9758
| ImV=-30*REI= |  | -1124.4038
V = SQRT(ReV*ReV + ImV*ImV)
|  |  | 3289.136 | Volts | Answer
Back to top of page
Prob.2.6 | Synchronous generator -Parallel operation-Example 2
Two 500 kVA alternators operate in parallel to supply the following loads
(a) 250 kW at .95 pf lagging
(b) 150 kW at .85 pf lagging
(c) 300 kW at .75 pf lagging
(d) 100 kW at .85 leading
One machine is supplying 400kW at .9 pf lagging .Calculate the power factor of the
other machine.
Solution; | Load power factors
| Cos f |  | Sin f | Load kW | Load kVAr = load kW*Sin f/Cos f
| 0.95 | lag | -0.31225 | 250 |  | -82.171
| 0.85 | lag | -0.52678 | 150 |  | -92.9617
| 0.75 | lag | -0.66144 | 300 |  | -264.5751
| 0.85 | lead | 0.52678 | 100 |  | 61.9744
|  | Total kW = | 800 | Total kVAr = |  | -377.7334
| Machine 1 pf |  |  | Machine 1 kW |  | Machine1 kVAr
| Cos f |  | Sin f
| 0.9 | lag | -0.43589 | 400 |  | -193.7288
Machine 2 KW
400
Machine2 KVAr = Total kVAr-Machine1 kVAr
-184.0045
|  |  |  | Machine 2 kVA = |  | 440.2927
Machine2 pf=Machine2 kW/Machine2 kVA
|  |  | 0.90849 | lag | Answer
Back to top of page
Prob.2.7 | Synchronous motor-Power factor improvement
A factory takes 600 kVA at a lagging power factor of 0.6. A synchronous motor is to be
installed to raise the power factor to 0.9 lagging when the motor is taking 200 kW.
Calculate the corresponding apparent power (in kVA) taken by the motor and the power
factor at which it operates .
Solution:
Q2, kVAr
P1=360 kW
|  | f |  | P2=200 kW
Q1=480 kVAr
600 kVA
Load power factor, Cos f=
0.6
| Sin f |  | 0.8
| Load kVA = |  | 600
P1,Load power = load kVA*cos f
|  |  | 360 | kW
Q1,Load reactive power = kVA*Sin f
|  |  | 480 | kVAr
| P2,Motor power = |  | 200 | kW
| Overall pf, Cos a= |  | 0.9 | lag
| tan a = |  | 0.48432
Since, tan a =(Q1-Q2)/(P1+P2),
| Q2=Q1-(P1+P2)tana |  | 208.7796 | kVAr
S2,Apparent power of the motor = sqrt(P2*P2+Q2*Q2)
|  |  | 289.1175 | kVA | Answer
| Motor pf=P2/S2= |  | 0.69176 | lead | Answer
Back to top of page
Prob.2.8 | Synchronous motor-excitation voltage & torque
A 55.95 kW ,3-phase,6-pole,60 Hz ,star-connected, cylindrical motor has a synchronous
reactance of 9.6 ohms/phase. Its rated terminal voltage is 500 V/phase. Find the value of
of excitation voltage that makes maximum torque to be 120 % of the rated torque.
Solution:
| P, No. Of poles |  | 6
| f, frequency |  | 60
| N,speed,rpm=120*f/P |  | 1200
| Rated power = |  | 55.95 | kW
| Rated power/phase = |  | 18.65 | kW
Rated torque =(60*Rated power)/(2*3.1416*N)
|  |  | 0.44523 | kN-m
Rated maximum power/phase = EV/Xs
Rated max. power per phase = Rated max. torque per phase*2*3.1416*N/60
=1.2* Rated torque per phase*2*3.1416*N/60=
|  |  | 22.38 | kW
E = Excitation voltage /phase
V = Terminal voltage /phase =
500
Xs = synchronous reactance, ohms =
9.6
E = Rated max. power per phase* Xs/V
|  |  | 429.696 | Volts | Answer
Back to top of page
Prob.2.9 | Synchronous motor-Operation
A 74.6 kW,3-phase,6-pole,60 Hz star-connected synchronous motor has synchronous
reactance of 10 ohms per phase. The rated terminal voltage is 1000V /phase.
(a) Find the excitation voltage that makes maximum torque to be 130 % of the rated
torque.
(b) The machine is operated with the excitation voltage set as in part (a).For rated load
torque, find the armature current, the power factor ,and the torque angle.
Solution : | f, frequency = |  | 60
| No. of poles = |  | 6
| N,speed=120f/poles |  | 1200 | RPM
| Prated = Rated power |  | 74600 | W
Trated = Rated tirque=60Prated/2*3.1416*N
|  |  | 8437080960 | N-m
| Trated/phase = |  | 2812360320 | N-m
V = terminal voltage/phase =
|  |  | 1000 | volts
Xs = synchronous reactance/phase =
|  |  | 10 | ohms
Pmax per phase =1.3 Prated per phase =
|  |  | 32326.6667 | W
| Pmax = EV/Xs |  | Therefore,
| E = Xs. Pmax/V= |  | 323.2667 | Volts
| Prated per phase = |  | 24866.6667 | W
Prated = Pmax Sin d
d = Asin(Prated /Pmax)=
|  |  | 0.87764 | radians
|  |  | 50.2847 | deg.
| V = E+j Ia. Xs | Therefore,
| Ia =(V-E)/jXs |  | =(1000+j0-Ecosd+jEsind)/jXs |  | Note:E lags V by d for a motor
| Re Ia = Esin d/Xs = |  | 24.8667
| Im Ia = |  | (-1000+Ecos d) /Xs
-71.6289
| Ia = |  | 75.8225 | Amps | Answer
| cosF = Re Ia/Ia |  | 0.32796 | lag | Answer
Back to top of page
Prob.2.10 | Synchronous motor- operation in parallel with a resistive load
A 3-phase star-connected load takes 50 A current at .707 lagging power factor at 220 v
between the lines. A 3-phase star-connected round rotor synchronous motor, having a
synchronous reactance of 1.27 ohms per phase is connected in parallel with the load.
The power developed by the motor is 33 kW at a power angle of 30 deg. Neglecting
armature resistance ,calculate
(a) reactive kVA of the motor ,and
(b) the overall power factor of the motor and the load.
Solution; |  |  | I |  | IL
| V |  |  | Motor |  | Load
Circuit Diagram
Ia
Phasor Diagram
Ia
I
|  |  | a | a1 | V
|  | f |  | d
|  |  | IL |  |  | jIa. Xs
| Cos f = |  | 0.707
| Sin f = |  | 0.70721 |  |  | E
| IL = load current = |  | 50 | A
| V(L-L) |  | 220 | Volts
| V per phase = |  | 127.0171 | Volts
| P, motor Power/phase = |  | 11000 | W
| Xs = |  | 1.27 | ohms
| d = load angle, deg= |  | 30
|  | radians = | 0.5236
| P = VE Sin d/Xs |  | Therefore,
| E = P Xs/VSind |  | 219.9699 | Volts
E Cosd = V+ Ia Xs Cosa
|  |  |  | E Sind = Ia Xs Sina |  | Therefore,
| Ia*Ia*Xs*Xs=E*E+V*V-2EVCosd |  |  |  | substituting for Xs,E,V,Cosd, we get
| Ia= |  | 99.993 | Amps | Answer
Cosa = motor pf = P/V. Ia |  |  | 0.86609 | lead | Answer
| Sina= |  | 0.4999
| Motor kVAr = |  | 1.73*VIaSin(a)=
|  |  | 19047.2255 | Var | Answer
| Overall power factor angle is given by |  |  | tana1=(Ia .Sina- IL. Sinf)/(Ia. cosa+ IL.Cosf)
| tana1= |  | 0.11993
| Overall pf = |  | 0.99289 | lead | Answer
Back to top of page
Prob.2.11 | Synchronous motor-induced emf & mechanical power developed
A 74.6 kW 400 V 1200 RPM ,3-phase Y-connected synchronous motor has an armature
resistance of 0.05 ohm per phase and a leakage reactance of 0.5 ohm per phase. At
rated load and 0.8 pf leading current, determine,
(a) induced armature emf E per phase at rated load
(b)angle between current and E
(c) mechanical power developed within armature at rated load.
The motor has a rated load efficiency ,excluding field loss of 90%.
Solution; | Efficiency = |  | 0.9
| Output = |  | 74600 | W
| Input Power = |  | 82888.8889 | W
| Voltage(L-L)= |  | 400 | V
| Voltage/phase = |  | 230.9402 | V
| Pf = cos f |  | 0.8 | lead
| Sin f |  | 0.6
| current = |  | 149.5498 | A
Phasor Diagram
| a | = f+d | I
a
|  |  | f |  |  | V
|  |  | d |  |  | IX
[5 empty] | E | IR
| R= |  | 0.05 | ohm
| X= |  | 0.5 | ohm
tan a = (V.sinf+ IX)/(V .cosf-IR)
1.2034
| a, deg = |  | 50.2749 |  | Answer
E= V- IZ= V-(I cosf+j Isinf)(R+j X)
ReE = V-IRcosf+IXsinf =
269.8232
| ImE = -IXcosf+ IRsinf |  | -55.3334
| E= |  | 275.4384 | Volts | Answer
Mechanical, Power =3EICosa
|  |  | 79019.848 | Watts
also Mechanical power = Input power-3I*Ir=
|  |  | 79534.1163 | Watts | Answer
Back to top of page
Prob.2.12 | Synchronous motor -maximum torque
A 1492 kW ,unity power factor,3-phase ,star-connected ,2300 V ,50 Hz ,30 poles,
synchronous motor has asynchronous reactance of 1.95 ohm/phase. Compute the
max. torque in N-m which this motor can deliver if it is supplied from a constant
frequency source and if the field excitation is constant at the value which would result
in unity power factor at rated load.
Assume that the motor is of cylindrical rotor type. Neglect all losses.
Solution: | Rated kVA,3-phase= |  | 1492
Rated kVA per phase =
497.3333
Rated Voltage/phase = V =
|  |  | 1327.9062 | Volts
| Rated current, I = |  | 374.5244 | Amps.
Synchronous reactance, Xs =
|  |  | 1.95 | ohms
Phasor diagram:
|  |  | I |  | V
IXs
E
E = SQRT(V*V + I*I*Xs*Xs)=
|  |  | 1515.4887 | Volts
| Pmax = EV/Xs = |  | 1032.0138 | kW/phase
| P, No.of poles = |  | 30
| f, frequency = |  | 50 | Hz
| Speed,N=120f/P= |  | 200
Max. Torque, T= 60Pmax/(2 p N)
|  |  | 49.2749 | kN-m/ph
| 3-phase max.Torque = |  | 147.8247 | kN | Answer
Back to top of page
Prob.2.13 | Synchronous generator -Performance Chart
An alternator is rated at 60 MW, 11 kV, .8 pf lagging and has a synchronous reactance of 2
pu and negligible resistance. Choosing a 3-phase MVA scale of 1 cm = 10 MVA, draw the
performance chart for this machine and show on it the stability limit for underexcitation
allowing a safety margin of 10 %.
Solution: | Vbase |  |  | 11 | kV
| pf |  |  | 0.8 | lag
| MW |  |  | 60
| MVAb |  |  | 75
| Xbase | = Vbase*Vbase/MVAb |  | 1.6133 | ohms
| Xpu |  |  | 2 | pu
| X | = Xpu*Xbase |  | 3.2267 | ohms/ph
| Vph |  |  | 6.3509 | kV
| I | ,= Vph/X |  | 1.9682 | kA
| Leading Vars per phase = Vph*Vph/X= |  |  | 12.5 | MVAr
|  |  |  | 37.5 | MVAr | 3-phase
|  |  | A | 60 MW
E=2 pu
P
E=1 pu
| -37.46 MVAr | B |  | 0
Q
Load line .8 pf lag
AB is the stability limit line for underexcitation
Back to top of page
Prob.2.14 | Synchronous motor- Induced emf
A 3-phase 400 V synchronous motor takes 72.5 A at a pf of (I) .8 lead, and (ii) .8 lag.
Calculate the power supplied and the induced emf for the two cases . The motor
impedance /phase is .2 +j 3 ohms.
Solution: | V | per phase | 230.9402 | V
| I |  | 72.5 | A
| Cosf | =pf= | 0.8 | lag
power supplied in the two cases=1.73*V*I*pf/1000=
|  |  | 40.1836 | kW
(i) Leading pf
| R |  | 0.2 | ohm/ph
| X |  | 3 | ohm/ph
I
|  |  | f |  | V
|  |  | d |  | IR
| Sinf | = | 0.6 |  | IX
I = Icosf +j I sin f
| Z = R+j X |  |  |  | E
E = V-IZ
E= E cosd- jEsind
Ecosd = V-IRcosf+IXsinf |  |  | 349.8402
Esind = -IXCosf-IRSinf |  |  | -182.7
| E= |  | 394.6739
| E(L-L)= |  | 683.5949 | V | Answer
(ii) Lagging pf
IR
|  |  | f |  | V
d
I
E IX
| Sinf | = | 0.6
I = Icosf-j I sin f
Z = R+j X
E = V-IZ
E= E cosd- jEsind
Ecosd = V-IRcosf-IXsinf |  |  | 88.8402
Esind = -IXCosf+IRSinf |  |  | -165.3
| E= |  | 187.6611
| E(L-L)= |  | 325.0383 | V | Answer
Back to top of page
Prob.2.15 | Synchronous motor-salient-pole-maximum power
A 1492 kW ,unity power factor,3-phase, star-connected 220 0V synchronous motor has
reactance of Xd = 2 ohms and Xq = 1 ohm per phase. Neglecting losses ,compute the
maximum mechanical power in kW which this motor can deliver if it is supplied with
electric power from an infinite bus at rated voltage and frequency and if its field
excitation is constant that results in unity power factor at rated load.
Solution: | Voltage ,L-L |  | 2200 | V
| V | per phase | 1270.1712 | V
| kVA | per phase | 497.3333 | kVA
| I | rated | =(kVA/V)*1000=
| I |  | 391.5483 | A
Phasor diagram for full-load conditions:
| Xd |  | 2 | ohms
| Xq |  | 1 | ohm
Id
|  |  |  | I | V
d
|  |  |  | Iq |  | jIXq
a c
[5 empty] | E' | Eaf
E'= V-jI .Xq
| Re E' |  | =V
|  |  | 1270.1712 | Volts
| ImE' |  | =-I*Xq
|  |  | -391.5483 | Volts
| E' mag |  | 1329.1519 | Volts
| d |  | =atan(ImE'/Re E')
|  |  | -0.29902 | radians
|  |  | -17.1326 | deg.
| Sin(- d) |  | 0.29459
| Id |  | =I*Sin d
|  |  | 115.3443 | A
| a'c | length | =Id*(Xd-Xq)
| a'c |  | 115.3443
| Eaf |  | =E'mag+a'c
| Eaf |  | 1444.4962 | Volts
P=(Eaf*V*Sind/Xd)+V*V(Xd-Xq)Sin2d/2XdXq
| A |  | =Eaf*V/Xd
| A |  | 917378.7278
| B |  | =V*V(Xd-Xq)/(2*Xd*Xq)
| B |  | 403333.7094
| P=Asind+Bsin2d |  | Max.Power occurs when dP/dd= 0,that is ,when
| Acosdm+2Bcos2dm=0 |  | or, when
| cosdm |  | =(-A+sqrt(A*A+32*B*B))/(8*B)
| cosdm |  | 0.47781
|  |  | 61.4572 | deg
| dm |  | 1.0726 | rad
| Pmax |  | =Asindm+Bsin2dm
|  |  | 1144472.834 | W
Pmax,kW for 3 phases=
|  |  | 3433.4185 | kW | Answer
Back to top of page
Prob.2.16 | Synchronous machine-operation at maximum power
A generator having a synchronous reactance of .9 pu based on its own rating is connected
via a transmission line to a remote bus.The voltage of the remote bus is 1 pu.The line
reactance is j .15 pu per phase based on the machine MVA. The internal emf E of the
machine is kept at 1.35 pu
(a) Calculate the pull-out power of the machine when operated as a generator
(b)At the moment of pull-out ,calculate the reactive powers at the generator terminals and
at the remote bus.
(c )What is the terminal voltage of the generator at the moment of pull-out?
(d) Is the machine current overloaded at pull-out?
Solution: |  | Pg |  |  | Pbus | Vb=1pu
|  |  | Xs=j.9 | Xl=j.15ohm |  | Remote bus
Generator
|  | E=1.35V | V
E
I
j I.Xs
|  |  | d | V | j I.Xl
t
Vb=1
Pg=Pbus=EVSind/Xs= EVSin(90-t)/Xs=EVcost/Xs=V VbSint/Xl.Therefore,
| E |  | 1.35 | Volts
| Xl |  | 0.15 | ohm
| Vb |  | 1 | volts
| Xs |  | 0.9 | ohm
| tant= EXl/Vb.Xs |  | 0.225
| t |  | 0.22131 | radian
| d | (3.14/2)-t
| d |  | 1.3487 | radian
I=(sqrt(E*E+Vb*Vb))/(Xs+Xl)
| I |  | 1.6 | A | Answer
Ixs*Ixs=E*E+V*V-2EVCos(1.57-t)
This is a quadratic equation in V
aV*V+bV+c=0 where
| a |  | 1
| b | -2*Ecos(1.57-t)
| b |  | -0.59478
| c | E*E-I*I*Xs*Xs
| c |  | -0.25117
| V | =(-b+sqrt(b*b-4*a*c))/(2*a)
|  |  | 0.88015 | Volts | Answer
(a) Pull-out power=EVb/(Xs+Xl)=
|  |  | 1.2857 |  | Answer
| (b) Qg= |  | (EVCos (d )/Xs)-V*V/Xs
|  |  | -0.56991 | pu | Answer
Generator behaves like shunt reactor
Reactive power at bus (defined positive from bus),
| Qb= |  | Vb*Vb/Xl-(V*VbCos(t)/Xl
|  |  | 0.94208 | pu | Answer
©
| V= |  | 0.88 | pu | Answer
| I= |  | 1.6 | pu | Answer
Back to top of page
Prob.2.17 | A 500 kVA ,3300 V,3-phase alternator has a synchronous reactance of .25 pu.It is
delivering full load at .8 pf lagging.By changing the excitation, the emf is increased by 20 % at this load.Calculate the new current and the power factor.The alternator is connected to infinite busbars.
at this load.Calculate the new current and the power factor.The alternator is connected to
infinite busbars.
| kVA | per phase | 166.6667
| Voltage | per phase | 1905.2568
| V |  | 1 | pu | Terminal Voltage
| Xs |  | 0.25 | pu | Sync.Reactance
| I | full load | 1 | pu | current
| E |  | =V + j I * Xs |  | Excitation voltage
| Cosf | =pf | 0.8 | lag
| sinf |  | -0.6
| Re E |  | =V- I*Xs*Sinf
1.15
| Im E |  | =I*Xs*Cosf
0.2
| E mag= |  | 1.1673 | pu
On changing the excitation, the new labels are E',I',Cosf',Sinf',d'
E' leads V by d'
| E'=1.2*E= |  | 1.4007 | pu
| E' |  | =V+ j I' Xs
| Re E' |  | =V-I' *Xs*Sinf'
| Im E' |  | = I' * Xs*Cosf'
| I'*Cos f' |  | =ImE'/ Xs
=ImE'/ Xs
=1.4* Sind'/Xs
|  |  | =5.6 Sind' | since Xs=.25
| I'* Sinf' |  | =(V-Re E')/Xs
=4-5.6* Cos d'
Since power remains the same,
| I' Cosf' |  | =I*cosf
|  |  | 0.8 | =5.6* Sind'
| d' |  | 0.14335 | radian
| I'* Sinf' |  | =4-5.6* Cos d'
-1.5426
| I' |  | =sqrt(I'Cosf'*I'Cosf'+I'Sinf'*I'sinf')
|  |  | 1.7377 | pu | Answer
| Cosf' | new pf= | 0.46039 | lag | Answer
| I full load | Amps | =kVA/Voltage
|  |  | 87.4773 | A
| I' | Amps | 152.0067 | A | Answer
Back to top of page
Prob.2.18 | A 3-phase generator supplying 2800 kW at power factor .7 lagging is loaded to its full
capacity ,i.e. its maximum rating in kVA.If the power factor is raised to unity by means of
an overexcited 3-phase synchronous motor, how much more active power can the
generator supply and what must be the power factor of the synchronous motor,
assuming that the latter absorbs all extra power obtainable from the generator?
Sketch the phasor diagram.
Solution: |  |  | I
|  |  |  | I1 | I2
| G |  | Load |  |  | M
| kW | per phase | 933.3333
| Cosf1 | pf | 0.7 | lag
| kVA | per phase | =kW/cosf1
1333.3333
| full load | per phase | =kVA per phase=
|  |  | 1333.333 | kW
Generator can supply an additional power
| P2 |  | =1333.333-933.333=
|  |  | 400 | kW/phase
|  | = | 1200 kW(3-phase) |  | Answer
Phasor diagram
I2
|  |  | f1 |  | V
|  |  | f2 | I
I1
Q2
|  |  | P1=933.333kW | f2
|  |  | f1 | P2=400 kW
Q1
| tanf1 |  | 1.0202
| Q1 | =P1tanf1 | 952.1901
| Q2 | =P2tanf2 | =400tanf2
Since Q1=Q2,
| tanf2 |  | 2.3805
| f2 |  | 1.1731 | radian
| cos f2 |  | 0.3873 | lead | Answer
Back to top of page
Prob.2.19 | Synchronous generator-Regulation from Magnetization curve
The magnetization curve of a 400 V 50 Hz alternator is given by the following readings:
| Open circuit, Volts: |  | Field current:A
| 266 |  | 2
| 334 |  | 2.5
| 377 |  | 3
| 422 |  | 3.5
| 450 |  | 4
| 484 |  | 4.5
| 508 |  | 5
Full - load current is obtained by 2A excitation on short-circuit. Calculate the percentage
regulation at .8 pf lagging
Solution: |  | 600
O/C Volts(L-L)
400
200
|  |  | 0 3.3 5 | If, Amps
To obtain a normal voltage of 400 V an excitation of 3.3 A is required
Excitation required to obtain normal voltage
|  |  | 3.3 | A
Excitation require to obtain rated current
|  |  | 2 | A
Short-circuit Ratio= Excitation required to obtain normal voltage/Excitation require to obtain
rated current
1.65
| Xs | Syn.Reactance= 1/short-circuit Ratio
| Xs |  | 0.60606 | pu
E
| Phasor diagram |  |  |  | I.Xs
V
f
I
| Vbase | = | 400/1.73205 | Volts
|  | = | 230.9402
| V | = | 1 | pu
| I | = | 1 | pu
| Xs | = | 0.606 | pu
| Cos f |  | 0.8
| Sin f |  | 0.6
| E | = | =SQRT((V*Cosf)*(V*Cos f)+(V*sinf+I*Xs)*(V*sinf+I*Xs)) | pu
| Epu |  | 1.4472
| E | Volts= | Epu*Vbase
334.2205
| Regulation= |  | =(E-V)/V
0.44722
|  | = | 44.72% | Answer
Back to top of page
Prob.2.20 | Synchronous motor-Current & Power factor
A 400 V 3-phase star-connected synchronous motor takes 3.73 kW at normal voltage , and
has an impedance of 1+ j8 ohms/phase.Calculate the current and the pf if the induced emf
is 460 V
Solution: | In this problem,E is greater than V.Therefore ,pf is leading.
I
|  |  | f | V
| Phasor diagram: |  | d | IR
IX
E
| V | per phase | 230 | V
| R |  | 1 | ohm
| Xs |  | 8 | ohm
| Cosf | pf
I=Icosf +j I sin f
| P | Power-3 ph | 3730 | W
| I1=Icosf =P/(3*V) |  | 5.4058 | A
| E | L-L | 460 | V
| E | per phase | 265.896 | V
I
|  |  |  | R | Xs
|  |  | E |  |  | V
I2=I Sinf
Z=R+j X
E=V-IZ
E= E cos d - jEsin d
E cos d =V-Ircos f +Ixsin f =V-RI1+XI2
Esin d =-IXCos f -IRSin f =-XI1-RI2
| E*E=(V-I1R+I2X)*(V-I1R+I2X)+(XsI1+RI2)*(XsI1+RI2) |  |  |  | -------------- | Eq.1
| P=3*V*I1 |  |  |  | -------------- | Eq.2
Eliminate I1 from Eqs.1 an2 respectively,and obtain
E*E= (V-(RP/3V)+XsI2)*(V-(RP/3V)+XsI2)+((XsP/3V)+RI2))*((XsP/3V)+RI2))
This is a quadratic equation in I2
aI2*I2+b*I2+c=0, where
| a=R*R+Xs*Xs |  | 65
| b=2*VXs |  | 3680
c=V*V-E*E -(2*R*P/3)+(R*RP*P/(9*V*V))+(Xs*Xs*P*P/(9*V*V))
-18387.8531
I2=(-b+sqrt(b*b-4*a*c))/2a
Therefore,
| I2=Isinf |  | 4.6197
| I1=I Cosf |  | 5.41
| I= sqrt(I1*I1+I2*i2) |  | 7.1141 |  | Answer
| Cosf | =I1/I= | 0.76046 | lead | Answer
Back to top of page
Prob 2.21 | Synchronous generator-Salient pole-Performance
A 6.6 kV 5 MVA 6-pole 50 Hz star-connected generator has Xd= 8.7 ohms/phase, Xq =4.35
ohms/phase. If the excitation is so adjusted that the excitation voltage Ef = 1.1 kV(L-L),
and the load angle is 30 deg.(elec.), determine
(a) the power factor,output current,and power in per unit
(b) the load angle at maximum torque
(c) the ratio between maximum torque and that occuring with d= 30 deg.
(d) the stiffness in Nm per mechanical radian for a load angle of 30 deg.
Solution: | (a)
| kVA | per phase | 1666.6667
| V | per phase | 3815.0289
| Ifl |  | =kVA*1000/V=
|  |  | 436.8687 | A
| load angle |  | 30 | deg
| d |  | 0.52333 | radian
| Sin( d ) |  | 0.49977
| Xd |  | 8.7 | ohms
| Xq |  | 4.35 | ohms
| Ef | per ph | 635.8382 | Volts
| Iq |  | =V*sin (d) /Xq
|  |  | 438.3074 | A
| Id |  | =(Ef-V*COS( d ) )/Xd
-306.7333
| I |  | =sqrt(Id*Id+Iq*iq)
|  |  | 534.9755 | A
| Ipu |  | =I/Ifl
|  |  | 1.2246 | pu | Answer
I Cos f = Iq cosd +Id sind
| cos f |  | =( Iq cosd +Id(magnitude) sind)/ I
|  |  | 0.99619 | lag | Answer
| P | Power | =Vpu*Ipu*Cosf
|  |  | 1.2199 | pu | Answer
(b)
| T |  | =(VEf Sin (d)/Xd)+(V*V/2)((1/Xq)-(1/Xd)) *Sin(2*d)
Differentiating this expression with respect to d and putting it equal to zero gives
| Cos (d) |  | =-(Ef/2*V)*(Xq/(Xd-Xq)) + sqrt((Ef/(2*4*V))*(Ef/(2*V))*(Xq/(Xd-Xq))*(Xq/(Xd-Xq)) -.5)
| Ef/(2*V) |  | 0.083333
| Xq/(Xd-Xq) |  | 1
Therefore
| Cos (d) |  | 0.45833
| (d) | max.value | 62.7522 | deg | Answer
|  | = | 1.0952 | radians
| dmax | = | 1.0952
| Sin(d) |  | 0.88904
| Sin(2*d) |  | 0.81407
(c)
| Tmax= |  | =(V*Ef*(Sin (dmax))/Xd)+(V*V/2)*(SIN(2*dmax))*(Xd-Xq)/(Xd*Xq)
928818.9129
| Trated= | at 30deg. | 863521.8388
| Tmax/Trated= |  | 1.0756 |  | Answer
| f | frequency | 50
| p | pole pairs | 3
| ns | =f/p | 16.6667 | rev/s
| ws | =2 p ns= | 104.6667 | rad/sec
(d)
| dT/d d | = | (V*Ef*Cos( d ) /Xd + (V*V*(Xd-Xq)/(Xd*Xq))*Cos(2 d ))/ws
| at 30 deg. | = | 10306.3787 | per phase
| for 3-phases |  | 30919.136 | Nm per electrical radian
|  |  | =30919.1359*p= | Nm per mechanical radian
|  |  | 92757.4077 | Nm per mechanical radian |  |  | Answer
Back to top of page
Prob.2.22 | Synchronous generator -Parallel operation-Example 3
Two identical16.66MVA,11 kV 3phase alternators are in parallel equally excited and
sharing equally a load of 25 MW at 11 kV and .8 pf lagging. Calculate the excitation at
rated voltage of each alternator assuming a constant synchronous reactance per phase of
1.08 pu.
If the excitation voltage of one alternator is to be reduced by 15 % , determine by how much
the excitation voltage of the the alternator must be increased , in order to avoid a
change of terminal voltage and of water supply to either set.
|  | I1 | jX |  | jX | I2
Solution:
I
| E1 |  | V | Load |  |  | E2
| I1= (E1-V)/jX |  | I2= (E2-V)/jX |  | I=I1+I2
I =(E1/jX) +(E2/jX)-(2V/jX)
| V= (E1+E2-IjX)/2, |  | (V/jX)=(E1/2jX)+(E2/2jX)-(I/2)
I1= E1((1/jX)-(1/2jX))-(E2/j2X) +(I/2)=( (E1-E2)/2jX)+I/2
I2= E2((1/jX)-(1/2jX))-(E2/j2X) +(I/2)=( (E2-E1)/2jX)+I/2
Circulating current
Here E1=E2
I1=I2=I/2
| P | Load | 25 | MW
| V | L-L | 11 | kV
| pf |  | 0.8 | lag
| I |  | 1642.144 | A
| I1 |  | 821.072 | A
| I2 |  | 821.072 | A
| MVAb | base | 16.66 | MVA
| Vb | base | 11 | kV
| Ib | base | 875.4598 | A
| I1pu |  | 0.93788
| I2pu |  | 0.93788
| Vpu |  | 1
E1=V+jI1*X
| X |  | 1.08 | pu
| Re E1 | =V+I1*sinf *X
|  | = | 1.6077
ImE1 | =I1*Cosf*X |  | 0.81032
| E1mag |  | 1.8004 | pu
| E1 angle |  | 26.7487 | deg
| d |  | 26.7487 | deg
Phasor diagram
E1=E2=E
I1X=I2X
d
|  |  | f | V
I1=I2=I/2
When the excitation of machine 1 is reduced so that E1' < E2', a circulating current Ic =
( E2'-E1')/j2X flows out of machine 2 and -Ic flows out of machine 1,ie
I1'=( I/2)-Ic, I2'= I/2 +Ic
Since the water supply to neither prime mover is changed , Ic must be in quadrature with
V.
E1=E2=E
|  | Ic | E1' | -IcX |  | IcX
[5 empty] | I1X=I2X | E2'
d
|  |  | f | V
I1'
Ic
I1=I2=I/2
I2'
E1'= E1-(-jIc)(jX)
ReE1'=ReE1-Ic*X
ImE1'=ImE1
| E1'mag | =.85E1mag |  | 1.5303
E1'mag=sqrt((ReE1-IcX)*(ReE1-IcX)+ ImE1*ImE1)= sqrt(ReE1*ReE1+Ic*Ic*X*X-2*ReE1*IcX+
ImE1*ImE1)
| ReE1= |  |  | 1.6077
| ReE1*ReE1= |  |  | 2.5848
| ImE1*ImE1= |  |  | 0.65663
| ReE1*ReE1+ImE1*ImE1= |  |  | 3.2415
| 2*ReE1*X= |  |  | 3.4727
| X*X = |  |  | 1.1664
Therefore,
| 1.1664Ic*Ic-3.241Ic+3.472725= |  |  | 2.342
Quadratic a*Ic*Ic+b*Ic+c=0 where
| a= |  |  | 1.1664
| b= |  |  | -3.2415
| c= |  |  | 0.89951
Therefore,
| Ic= |  |  | 2.4664
E2'=E1+2*Ic*jX=ReE1+j ImE1+2jIc*jX
| ReE2'= |  |  | =ReE1-2Ic*X
-3.7196
| ImE2'= |  |  | =ImE1
0.81032
| E2'mag |  |  | 3.8068 | pu | Answer
Back to top of page