## Sheet1
CHAPTER 5
Underground Cables Problems
with Solutions
Problems |  | Topics
5.1 |  | Underground cable-3-core-Tests to determine capacitances
5.2 |  | Underground cable-3-core-Charging kVA
5.3 |  | Underground cable-single core- Charging kVA
5.4 |  | Underground cable-single-phase operation of a 3-core cable
5.5 |  | Underground cable-single core-Insulation resistance
5.6 |  | Underground cable-electrostatic stress
5.7 |  | Underground cable-condition for maximum electric stress to be minimum
5.8 |  | Underground cable-Temperature rise of conductor & sheath
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.5.1 | Underground cable-3-core-Tests to determine capacitances
In a test of a 3-conductor underground cable ,shown in Figure below,
C1
C2
the 3 conductors are bunched together, and the capacitance between the bunched
conductors and the sheath is found to be Ca. The capacitance between two of the
conductors bunched together with the sheath , and the third conductor is found to be Cb.
Determine C1 and C2 for the cable, in tems of Ca and Cb.
Solution: | Ca |  | =3*C1
| Cb |  | =C1 + 2*C2
Therefore,
| C1 |  | =(1/3)*Ca |  |  | Answer
| C2 |  | =(1/2)*(Cb- (1/3)*Ca) |  |  | Answer
Top of Page
Prob.5.2 | Underground cable-3-core-Charging kVA
In a 3-core cable, the capacitance between the cores short-circuited together and the sheath
is 0.54 microfarad/km and that between two cores connected together and the third core
is 0.52 microfarad /km. Determine the kVA required to keep 10 km of the cable charged
when the supply is 33kV ,3 phase ,50 Hz.
Solution:
C1
C2
| Ca | = Capacitance between the three cores bunched together and the sheath
| Ca |  |  | 0.54
| Cb | =capacitance between two cores connected together and the third core
| Cb |  |  | 0.52
From the solution of Prob.5.1, we have
| C1 |  |  | =(1/3)*Ca
0.18
| C2 |  |  | =(1/2)*(Cb- (1/3)*Ca)
0.17
| Equivalent circuit: star | [5 empty] | C1 +3C2
| Capacitance /phase |  |  | =C1+3*C2
| Co |  |  | 0.69 | microfarad/km
| Co |  |  | 6.9e-07 | Farad/km
| V(L-L) |  |  | 33 | kV
| f |  |  | 50 Hz
| w |  |  | 314.16 | rad/s
| l | cable length |  | 10 | km
| kVA | 3-phase |  | =V(L-L)*V(L-L)w*Co*l*1000
|  |  |  | 2360.6297 | kVA |  | Answer
Top of Page
Prob.5.3 | Underground cable-single core- Charging kVA
A single-phase concentric cable2.4 km long is connected to 50 Hz,6.6 kV busbars. The
inner conductor has a diameter of 1.25 cm and the radial thickness of insulation is
.8 cm. The relative permittivity of the dielectric is 3.5. Determine the charging kVA.
Solution: | [5 empty] | Outer dia ,D
Core dia, d1= 1.25 cm
| d1 | core dia |  | 1.25 | cm
| t | radial thickness |  | 0.8 | cm
| D | Outer dia |  | 2.85 | cm
| w | angular frequency |  | 314 | rad/s
| l | cable length |  | 2400 | m
| er | permittivity |  | 3.5
| eo | permittivity-free space |  | 8.8419e-12
| ln(D/d1) |  |  | 0.82418
| C | Capacitance |  | =(2*3.1416*eo *er*l)/ln(D/d1)
|  |  |  | 5.6622e-07 | F
| V |  |  | 6600 | Volts
| charging kVA |  |  | =V*V*w*C/1000
|  |  |  | 7.7447 | kVAr | Answer
Top of Page
Prob.5.4 | Underground cable-single-phase operation of a 3-core cable
A single-phase voltage of 10kV at a frequency of 50 Hz is applied between two of the cores
of a 3-phase belted cable. The core -to -core capacitance is 0.15 microfarad and the core -to
sheath capacitance is .1 microfarad. Calculate
(a) the potential difference between the third core and the sheath, and
(b) the total charging current taken by the cable.
Solution: | [6 empty] | Cs
Cc
[5 empty] | S | ,Sheath
Cc
Cs
S
|  |  |  | 3Cc | Cs
|  |  | Cs |  | 3Cc
3Cc Cs
|  |  | R |  |  | R
Cs+3Cc
(Cs/2)+3Cc/2
S
|  |  | Cs+3Cc |  |  | Ic
B
|  | B |  | Y
| Voltage between Y (third core ) and sheath= zero |  |  |  |  | Answer
Single-phase voltage is applied between R and B
| V |  |  | 10000 | Volts
| w |  |  | 314
| Cs |  |  | 1e-07 | F
| Cc |  |  | 1.5e-07 | F
| Ic | Current = V w ((Cs/2)+3Cc/2)
|  |  |  | 0.8635 | A | Answer
Top of Page
Prob. 5.5 | Underground cable-single core-Insulation resistance
A cable composed of a conductor of 2 mm diameter covered with 1 mm of insulating
material is found to have an insulation resistance of 480 megohms per km. What thickness
of a similar material would be required for a 3mm diameter conductor in order to have an
insulation resistance of 960 megohm per km?
Solution: | d1 | conductor dia |  | 2 | mm
| t1 | insulation thickness |  | 1 | mm
| d2 | cable dia=d1+2t1 |  | 4 | mm
| R | Insulation resistance = |  | (r*ln(d2/d1))/2*p
| R |  |  | 480 | megohms/km
| R2 | New insulation resistance
|  |  |  | 960 | megohms/km
| d2' | New cable dia
| d1' | New cond.dia |  | 3 | mm
| R2 |  |  | =R*ln(d2'/d1')/ln(d2/d1)
| ln(d2'/d1') |  |  | =R2*ln(d2/d1)/R
1.3863
| d2' |  |  | =d1'*exp(lnd2'/d1)
12
| t2 | new thickness |  | =(d2'-d1')/2
|  |  |  | 4.5 | mm | Answer
Top of Page
Prob.5.6 | Underground cable-electrostatic stress
A single-core cable for use on 11 kV 50 hz system has conductor area of .645 cm*cm.
The internal diameter of the sheath is 2.18 cm.The permittivity of the dielectric is 3.5. Find
the maximum and minimum electrostatic stresses in the cable.
Show the curve of stress distribution in the cableversus distance from the centre of the
conductor.
Find the capacitance of the cable per km length.
Find the charging curent.
Solution: | Ex= q/2 p eo er x |  | (V/m)
g=potential gradient= electric field intensity=Ex
r2
| Potential differencre between core and sheath = |  |  |  | Ex. Dx | =qln(r2/r1)/2p eo e r
r1
| C=q/V= | =2p eo e r/ln (r2/r1)
| q= | =2p eo e rV/ln (r2/r1)
| g= |  |  | V/x ln(r2/r1) | V/m
| gmax |  |  | V/(r1ln(r2/r1))
| gmin |  |  | V/(r2ln(r2/r1))
| V |  |  | 11000 | Volts
| A | conductor area |  | 0.645
| r1 | conductor radius |  | 0.45311 | cm
| r2 |  |  | 1.09 | cm
| gmax |  |  | 27656.3289 | V/cm
| gmin |  |  | 11496.6801 | V/cm
r1
r2
gmax
g
gmin
|  |  | r1 r2 | x
| er |  |  | 3.5
| eo |  |  | 8.8419e-12
| C=q/V= | =2p eo e r/ln (r2/r1) |  | 2.2151e-07 | F/km | Answer
| w |  |  | 314
| I=wCV |  |  | 0.76511 | A | Answer
Top of Page
Prob.5.7 | Underground cable-condition for maximum electric stress to be minimum
Show thatfor agiven voltage , the maximum stress Emax in the dielectric of asingle -core
cable the sheath diameter D is a minimum when D= ed where d is conductor diameter
and e is the base of natural logarithms. Determine D and d for V= 10 kV and Emax =
23 kV/cm
Solution: | g max= V/r1 ln (r2/r1)
gmax is minimum when r1ln(r2/r1) is maximum I.e when r2=e r1or D= e.d
| min.gmax | =gmax=Emax |  | 23 | kV/cm
| V |  |  | 10 | kV
min gmax=V/r1
Therefore,
| r1 | =V/min gmax |  | 0.43478
| d | =2r1 |  | 0.86957 | cm | Answer
| D | =e*d |  | 2.3637 | cm | Answer
Top of page
Prob.5.8 | Underground cable-Temperature rise of conductor & sheath
Three 132 kV single -core cables rated at 600 A are laid at a depth of 100 cm in horizontal
formation5 cm apart. The thermal resistivity of the soil is 100 (deg.C-cm/W).The cable
details are:
| copper conductor |  |  | 3 cm*cm cross-section
| Insulation |  |  | 1 cm in radial thickness
Outer radius 2 cm
g=500 deg C -cm/W
| Laed sheath |  |  | Thickness .2 cm
g= 3 deg C-cm/W
| Covering |  |  | Thickness=.6 cm
g= 500 deg C-cm/W
Rated load copper loss at 85 deg C is .3 W/cm.
Dielecric loss per cm is .02 W/cm
Cables are cross-bonded. Sheath loss is negligible
Calculate the temperature rise of the conductor and sheath if the ambient temperature is 15
deg.C
Solution:
|  | Dielectric loss |  | sheath loss
|  | Rd/2 | Rd/2 | Rsh | Rcovering | Rsoil
| q conductor |  | q sheath
| R | insulation outer radius |  | 2 | cm
| t | insulation thickness |  | 1 | cm
| r | insulation inner radius |  | 1 | cm
| R | sheath inner radius |  | 2 | cm
| t | sheath thickness |  | 0.2 | cm
| R1 | sheath outer radius |  | 2.2 | cm
| t1 | covering thickness |  | 0.6 | cm
| R2 | cable radius |  | 2.8 | cm
| g1 | g of insulation |  | 500 | degC-cm/W
| g2 | g of sheath |  | 3 | degC-cm/W
| g3 | g of covering |  | 500 | degC-cm/W
| g4 | g of soil |  | 100 | degC-cm/W
Thermal resistances of dielectric, sheath and covering are Rd, Rsheath, and R covering
| Rd | =g1*ln(R/r)/(2*p) |  | 55.1588 | degC/W
| Rsheath | =g2*ln(R1/R)/(2 * p ) |  | 0.045507 | degC/W
| Rcovering | =g3*ln(R2/R1)/(2 * p) |  | 19.191 | degC/W
| h | cable depth |  | 100 | cm
| p | cable spacing |  | 5 | cm
Thermal resistance of soil presented to the centre cable=R soil
| R soil | =g4Ln(2*h/R2)/(2 *p)+g4*ln((4*h*h+p*p))/(p*p)/(2*p)
|  |  |  | 185.4032 | degC-W/cm
| copper loss |  |  | 0.3 | W/cm
Conductor temperature rise=Copper loss *(Rd+Rsh+Rcovering+ Rsoil)
|  |  |  | 77.9396 | deg.C
| Dielectric loss |  |  | 0.02 | W/cm
Temp.rise due to dielectric loss=Dielectric loss*((Rd/2)+Rsh+R covering+ Rsoil)
|  |  |  | 4.6444 | deg .C
| Ambient temp. |  |  | 15 | deg.C
| Conductor temp. | =rise due to cu loss + rise due to dielectric loss +ambient temp.
|  |  |  | 97.5839 | deg.C
Top of page