## Sheet1
CHAPTER9
Short - circuit Problems
with Solutions
Prob.No. |  | Topic
9.1 |  | Short-circuit level of 4 alternators in parallel
9.2 |  | Fault current-single-phase fault on an alternator
9.3 |  | Short-circuit level for a fault on an 11 kV feeder of a power system
9.4 |  | Fault current and the voltage at the healthy phase for a line-line fault
at the remote end of a line connected to an alternator
9.5 |  | Generator supplying power to a synchronous motor via a transmission line-
To find fault currents in the machines for a 3-phase fault at the alternator terminals
9.6 |  | To find the reactance of the current limiting reactors to limit the fault current
9.7 |  | A generator supplying power to a motor:For the single phase fault at the
generator terminals,to find the fault current( in the faulted phase ) flowing into the
fault and the contributions of the generator & motor to the fault.
9.8 |  | Line-to-line fault at the terminals of a generator-To find fault current
9.9 |  | To find fault curent & voltages for a DLG fault at the terminals of an unloaded
generator
WEBSITE | takes you to the start page after you have read this Chapter.
Start page has links to other Chapters.
Prob.9.1 | Short-circuit level of 4 alternators in parallel
Four identical alternators ,each rated at 11 kV ,25 MVA, and each having a sub-transient
reactance of 16 5 on its rating , are connected in parallel to a common busbar. Find the
3-phase fault level at the outgoing feeder from the common busbar.
Solution: | Base kV |  |  | 11
| Base MVA |  |  | 25
| X'pu |  |  | 0.16
| pu fault MVA from one alternator |  |  | =1/X'pu
| pu fault MVA from one alternator |  |  | 6.25 | pu(MVA)
| Fault MVA |  |  | 156.25
|  |  |  | 156.25 | MVA
| number of alternators |  |  | 4
| Total fault MVA |  |  | 625 | MVA | Answer
Top of page
Prob.9.2 | Fault current-single-phase fault on an alternator
A 3- phase 33 kV,37.5 MVA alternator is connected to a 33 kV overhead line which
develops an earth fault at the remote end. The positive, negative and zero-sequence
reactances of the line are 6.3,6.3, and 12.6 ohms/conductor and those for the alternator are
are .18, .12 and .1 pu respectively. Calculate the fault current in kA, and the phase
voltages at the alternator terminals in kV. Assume the alternator star point is solidly earthed
Solution: | Base MVA |  |  | 37.5
| Base kV |  |  | 33
| Base I |  |  | 0.65686 | kA
| Base X |  |  | 29.04 | ohms
Alternator sequence reactance's
| X+pu |  |  | 0.18
| X-pu |  |  | 0.12
| Xopu |  |  | 0.1
| X+ |  |  | 6.3 | ohms
| X- |  |  | 6.3 | ohms
| Xo |  |  | 12.6 | ohms
| X + pu |  |  | 0.21694
| X-pu |  |  | 0.21694
| Xopu |  |  | 0.43388
Total reactance of three sequence networks in series=
|  |  |  | 1.2678 | pu
| E |  |  | 1 | pu
| I+=I-=Io= |  |  | =E/Total reactance
|  |  |  | 0.78879 | pu
| Fault current= 3*I+= |  |  | 2.3664 | pu
|  |  |  | 1.5544 | kA
Voltages w.r.t earth at alternator terminals are calculated using
| V+=E-I+*Z1 |  |  | 0.85802 | pu
| V-=-I-*Z2 |  |  | -0.094654 | pu
| Vo = -IoZo |  |  | -0.078879 | pu
| Va | =V+ +V- +Vo= |  | 0.68449 | pu
|  |  |  | 13.0412 | kV | Answer
| Vb | = a*aV + + a*V- + Vo
| Re Vb | =-.5V+ -.5V- +Vo |  | -0.46056
| Im Vb | =.866(V+- V-)= |  | 0.82501
| Vb mag |  |  | 0.94486 | pu
|  |  |  | 18.0021 | kV | Answer
| Vb angle |  |  | -60.8276 | deg | Answer
Vc
| Re Vc | =-.5V+ -.5V- +Vo |  | -0.46056
| ImVc | =.866(-V++ V-)= |  | -0.82501
| Vc mag |  |  | 0.94486 | pu
|  |  |  | 18.0021 | kV | Answer
| Vc angle |  |  | 60.8276 | deg | Answer
Top of page
Prob.9.3 | Short-circuit level for a fault on an 11 kV feeder of a power system
Calculate the fault level for a 3-phase symmetrical short-circuit on an 11 kV feeder
in the following system
Remainder of Grid
Grid infeed= 1500 MVA
132 kV
2 X 50 MVA,12.5 %
4 X 25 MVA,16%
|  |  |  | 11kV |  |  |  | 11kV
5.3 % on 25 MVA
F
| Generator reactance |  |  | 0.16 | pu
| Generator MVA |  |  | 25
| Transformer reactance |  |  | 0.125 | pu
| Transformer MVA |  |  | 50
| Reactor reactance |  |  | 0.053 | pu
| Reactor MVA |  |  | 25
| Grid infeed |  |  | 1500 | Mva
| Base MVA |  |  | 100
| Grid infeed on base MVA |  |  | 15 | pu
| E | Grid voltage |  | 1 | pu
| EI | Grid voltamp |  | 15 | pu
Grid source reactance (pu)=E/I = E*E/E*I
|  |  |  | 0.066667 | pu
| Generator reactance |  | on common base
|  |  |  | 0.64 | pu
| Transformer reactance |  | on common base
|  |  |  | 0.25 | pu
| Reactor reactance |  | on common base
|  |  |  | 0.212 | pu
Solution: | pu equivalent circuit
1 pu emf
j.0667
|  | j.64 | j.64 |  |  | j.64 |  | j.64
|  |  | j.25 |  | j.25
j.212
IF
Reduce the circuit by combining two parallel branches and converting delta into star as
follows:
1 pu emf
a
0.0667
b
0.0878
|  |  | 0.32 |  |  |  |  | 0.32
e
|  |  |  | 0.0743 | 0.0743
[5 empty] | c | d
IF
Further reduction gives
a
a
|  |  |  | 0.32 |  | 0.1105
[5 empty] | e |  | .117 pu
c
0.0743
c
IF
IF
|  | Fault MVA= |  |  | 100/.117
[5 empty] | 854.7009 | MVA | Answer
The circuit breaker will thus be rated at the next standard size 11kV,1000MVA
Top of page
Prob.9.4 | Fault current and the voltage at the healthy phase for a line-line fault at the remote end
of a line connected to an alternator
A 3- phase 33 kV 37.5 MVA alternator is connected to a 33 kV overhead line which
develops a short-circuit between phases b and c at the remote end . The positive
and negative sequence reactances are 18 and 12 % (on rating) while those for the line are
6.3 ohms each. Calculate the fault current , and the voltage of the healthy phase to earth
at the fault point.
Solution: | Base MVA |  |  | 37.5
| Base kV |  |  | 33
| Base X |  |  | 29.04 | ohms
| Xg+ |  |  | 0.18 | pu
| Xg- |  |  | 0.12 | pu
| Xl+ |  |  | 6 | ohms
| Xl- |  |  | 6 | ohms
| Xl+ |  |  | 0.20661 | pu
| Xl- |  |  | 0.20661 | pu
| X1 | Total positive sequence reactance = Xg+ +Xl+
|  |  |  | 0.38661 | pu
| X2 | Total negative sequence reactance = Xg- + Xl-
|  |  |  | 0.32661 | pu
Sequence network connections for a line to line fault
|  |  |  | f1 |  |  | f2
|  | Z1 |  | Ia1 |  | Z2 | Ia2
E
|  |  |  | Va1 |  |  | Va2
| E |  |  | 1 | pu
| Ia1 | =E/(X1+X2) | -j | 1.4021 | pu
| Ia2 | =-Ia1 | j | 1.4021 | pu
| Ib | =a*a* Ia1+a*Ia2=(a*a-a)Ia1, where a= -.5-j.866,(a*a-a)=-j1.732
| Ib |  |  | -2.4284 | pu
| Ib mag |  |  | 2.428 | pu
|  |  |  | 1.5949 | kA | Answer
| Ib angle |  |  | 180 | deg
At the point of fault (healthy phase -a),
| Va1 | =E-Ia1jX1 |  | 0.45794 | pu
|  |  | angle | 0 | deg
| Va2 | =Va1 |  | 0.45794 | pu
|  |  | angle | 0 | deg
| Vae | =Va1+Va2= |  | 0.91587 | pu
|  |  |  | 17.4498 | kV | Answer
|  |  | angle | 0 | deg
| Fault MVA=1.59485*33= |  |  | 52.6301 | MVA
Top of page
Prob.9.5 | Generator supplying power to a synchronous motor via a transmission line-
To find fault currents in the machines for a 3-phase fault at the alternator terminals
A 22 kV 100 MVA alternator with .25 pu transient reactance is supplying a load through a
transmission line of reactance .05 pu at 100 MVA. The load at a particular time is equivalent
to a 50 MVA synchronous motor with .2 pu transient reactance which is taking 40 MW
at .8 pf leading with a terminal voltage of 21.9 kV.
If a 3-ophase short-circuit occurs at the alternator terminals, calculate the current in each
of the two machines and in the fault during The transient period.
Solution: | MVAb | base value |  | 100
| kVb | base value |  | 22
| Ib | base value |  | 2624.3206 | A
| Pm | motor load |  | 40 | MW
| Vm | motor voltage |  | 21.9 | kV
|  |  |  | 0.99545 | pu
| pfm | motor pf |  | 0.8 | lead
| Im | motor current |  | 1318.1519 | A
|  |  |  | 0.50228 | pu
| Motor MVA |  |  | 50
| Xm | on equipment base |  | 0.2 | pu
| Xm' | on 100 MVA base |  | 0.4 | pu
| Xg' | 0n 100 MVA |  | 0.25 | pu
| Xl | line reactance |  | 0.05 | pu
0.05
| 0.25 |  |  |  | 0.4
|  | Vg |  | Vm
| Eg' | G |  | M |  | Em'
Vm is the reference phasor
| Re Im | = Im *pfm |  | 0.40183 | pu
| Im Im | =Im*Sin(acos(pfm) |  | 0.30137 | pu
| Vg | = Vm+jXl(Re Im +j Im Im)
| Re Vg | = Vm -Xl*ImIm |  | 0.98039 | pu
| Im Vg | =Xl *Re Im |  | 0.020091 | pu
Eg' = Vg+ jXg*(ReIm+jIm Im)
| Re Eg' | =Re Vg-Xg*Im Im |  | 0.90504 | pu
| Im Eg' | = ImVg + 'Xg'''*Re Im |  | 0.12055 | pu
Em' = Vm-jXm'*(ReIm+jImIm)
| Re Em' | =Vm+Xm*Im Im |  | 1.116 | pu
| Im Em' | =-Xm*Re Im |  | -0.16073 | pu
Total fault current during the transient period is found by superposition of Ig' and Im' which
flow through the switch.
| Ig' | =Eg'/jXg'
| Re Ig' |  |  | 0.48219 | pu
|  |  |  | 1265.4258 | A
| Im Ig' |  |  | -3.6202 | pu
|  |  |  | -9500.4982 | A
| Im' | =Em'/(jXm'+jXl)
| Re Im' |  |  | -0.35718 | pu
|  |  |  | -937.3525 | A
| Im Im' |  |  | -2.48 | pu
|  |  |  | -6508.3297 | A
Total current in each phase of the short-circuit:
| Real part= |  |  | 328.0734 | A | Answer
| Im Part= |  |  | -16008.8279 | A | Answer
Top of page
Prob.9.6 | To find the reactance of the current limiting reactors to limit the fault current
Three star-connected 11 kV alternators are connected each in series with a similar current-
limiting reactor to a common busbar. The alternators each have a rating of 10 MVA and
subtransient reactance per phase of .06 pu. Two 11/33 kV transformers of 15 MVA rating,
.03 pu reactance , and 10 MVA, .02 pu reactance respectively, connected in parallel to this
busbar, supply a transmission line of impedance .2 + j .7 ohms /km. At a substation 10
km from the generating station is a 25 MVA 33/11 kV transformer of .06 pu reactance.
Calculate the reactance of the current -limiting reactors if each alternator is not to carry
more than 2.333 times the full-load current, when a symmetrical short-circuit occurs on the
11 kV busbars in the substation.
Solution: | [5 empty] | Generators, Xg = .06 pu, 10 MVA
Reactors ,X
| Transformers,10 MVA, Xt1=.02 pu |  |  |  |  | 15 MVA, Xt2=.03 pu
Line Zpu = Rl+jXl = .2 +j .7 (ohms /km)
Transformer 25 MVA Xt3 =.06 pu
F
| MVAb |  |  | 25
| l | Line length |  | 10 | km
| Rl' | line resistance/km |  | 0.2 | ohms/km
| Xl' | line reactance /km |  | 0.7 | ohms/km
| Rl | =Rl'*l |  | 2 | ohms
| Xl | =Xl'*l |  | 7 | ohms
| Vb | in line |  | 33 | kV
| Rlpu | = Rl*MVAb/(Vb*Vb) |  | 0.045914 | pu
| Xlpu | =Xl*MVAb/(Vb*Vb) |  | 0.1607 | pu
| Xg' | on generator base |  | 0.06 | pu
| Xg | on common base |  | =.06*25*11*11/(10*33*33)
|  |  |  | 0.016667 | pu
| MVAt1 | transformer t1 rating |  | 10 | MVA | Xt1'= | 0.02 | pu
| MVAt2 | transformer t2 rating |  | 15 | MVA | Xt2'= | 0.03 | pu
| MVAt3 | transformer t3rating |  | 25 | MVA | Xt3'= | 0.06 | pu
| Xt1 | on common base |  | 0.05 | pu
| Xt2 | on common base |  | 0.05 | pu
| Xt3 | on common base |  | 0.06 | pu
pu Reactance diagram:
|  |  | 1 | 2 3 | 4 | I | 5
| 1=generator reactance of 3 generators in parallel= |  |  |  |  | 0.0055556 | up
2=reactance of 3 reactors in parallel=X/3, X is the unknown
| 3= reactance of two transformers in parallel= |  |  |  |  | 0.025 | pu
| 4= line Impedance= |  |  |  | R | 0.045914 | pu
[5 empty] | X | 0.1607 | pu
| 5= transformer reactance = |  |  |  | Xt3 | 0.06 | pu
| Total reactance |  |  | 0.25125 | +X/3
Total impedance= .0459+j(.251+X/3)
Fault current in the pu circuit=I=1/(.0459+j(.251+X/3))
Magnitude of fault current= Imag= 1/sqrt(.0459*.0459+(.251+X/3)*(.251+X/3))
Fault current in each alternator=Imag/3
| MVA rating of each alternator = |  |  | 10 | kV rating | 11
| Full load current of each alternator = MVA rating/1.74* kV rating= | [5 empty] | 524.8641 | A
| Ib | base current |  | 437.3868 | A
Full load current of each alternator, pu
|  |  |  | 1.2 | pu
Therefore this value times (7/3) should be equal to Imag/3 .
or,
.0459*.0459 +(.251+X/3)*(.251+X/3)= (1/8.4)*(1/8.4)
or,
| X= | 0.42347 | pu
| X ohms |  |  | 18.4464 | ohms | Answer
Top of page
Prob.9.7 | A generator supplying power to a motor: For the single phase fault at the
generator terminals,to find the fault current( in the faulted phase ) flowing into the
fault and the contributions of the generator & motor to the fault.
In the following figure, G is an exporting grid area(generator0 having a 3-phase fault level
of 20000 MVA at the 400 kV busbars S. The corresponding data for the grid imporing rea M
(motor) is 10000MVA at R. The short 400 kV line has a series reactance of 40 ohms /phase.
The load transfer is 150 MW, .8 pf lagging, 360 kV at R. If ahort circuit to earth occurs on
one phase at S, calculate the current (in phase A) flowing into the fault and the contributions
of the generator & motor to the fault current (in phase A).
|  |  |  | jXg | S | R | jXm
j40 ohms
G
M
For both area during the subtransient period, the negative and zero sequence reactances
may be assumed to be 100 % and 50 % respectively of the positive sequence values for
the grid areas and 100% and 20% for the line. Both G and M are solidly earthed.
Solution: | MVAg | fault, MVA of gen. |  | 20000 | MVA
| V | busbar Voltage |  | 400 | kV
| Ig | Gen fault current |  | 28.9017 | kA
| Xg | Source reactance |  | 7.9905 | ohm/ph
| MVAm | for motor |  | 10000 | MVA
| V | for motor |  | 400 | kV
| Im | for motor |  | 14.4509 | kA
| Xm | for motor |  | 16 | ohm/ph
Take VR as reference phasor
| VR | L-L |  | 360 | kV
|  | L-N |  | 207.8462 | kV/ph
| P | Load power |  | 150 | MW
| pf | load pf |  | 0.8 | lag
| Im | load current magnitude |  | 0.30106 | kA
| Re Im |  |  | 0.24085 | kA
| Im Im |  |  | 0.18064 | kA
| Xl | line reactance |  | 40 | ohms
| VS = Vr + ImIm * jXl |  |  | 208.0268 | kV/ph
| Re VS |  |  | 215.0716 | kV/ph
| Im VS | = Re Im *Xl |  | 9.6339 | kV/ph
This is the balanced pre-fault voltage at S……..= Vf
The following are generator , line and motor sequence reactances:
| Xg+ |  |  | 7.9905 | ohms
| Xg- |  |  | 7.9905 | ohms
| Xg0 |  |  | 3.9953 | ohms
| Xl+ |  |  | 40 | ohms
| Xl- |  |  | 40 | ohms
| Xl0 |  |  | 8 | ohms
| Xm+ |  |  | 16 | ohms
| Xm- |  |  | 16 | ohms
| Xm0 |  |  | 8 | ohms
The following shows thew sequence network for a single -line to ground fault.
Xg+ |  | Vf= VS
Xg-
Xg0
Xl+
Xl- | Xg+ | Xl+ |  | Xg- | Xl- |  | Xg0 | Xl0
|  | Xm+ |  |  | Xm- |  |  | Xm0
| Z1 | Z2 | Z0
=(Xg0*(Xl0+Xm0)/(Xg0+Xl0+Xm0)
=(Xg-*(Xl-+Xm-)/(Xg-+Xl-+Xm-)
=(Xg+*(Xl++Xm+))/(Xg++Xl++Xm+)
| Z1 |  |  | 6.9927 | ohms
| Z2 |  |  | 6.9927 | ohms
| Z0 |  |  | 3.197 | ohms
Fault current flowing from A phase conductors into the fault at S is
| Iae | =3*Vf/(Z1+Z2+Z0)
| Re Iae | =3*ImVf/(Z1+Z2+Z0) |  | 1.682 | kA
| Im Iae | =3*Re Vb/(Z1+Z2+'Z0')
|  |  |  | 37.5508 | kA
Real part of Positive sequence current in phase A fed into the fault from the generator is
|  |  |  | 0.49067 | kA
Imaginary part of Positive sequence current in phase A fed into the fault from the generator is
|  |  |  | 10.9539 | kA
and real part of positive sequence current from motor is
|  |  |  | 0.070013 | kA
and imaginary part of positive sequence current from motor is
|  |  |  | 1.563 | kA
Negative sequence currents are the same.
Real part of Zero sequence currents in A phase fed into fault from G is
|  |  |  | 0.44865 | kA
Real part of Zero sequence currents in A phase fed into fault from G is
|  |  |  | 10.0159 | kA
| and from motor is :Real part |  |  | 0.11203 | kA
| Imag.part |  |  | 2.501 | kA
To these fault currents must be added the load current which is wholly positive sequence
,in order to give the actual current in any part of the system.
The positive sequence current in phase A flowing from G is
=0.49067- j10.953+(0.24-j.18)=0.712-j10.74 kA
from M is .07-j1.56 -(.24-j.18)=-.173-j1.33 kA
Actual current in phase A flowing from G is =.712-j10.74+.472-j10.56+.517-j11.57
=1.7-j32.87 kA
and from motor is
=-0.173-j1.33+0.067-j1.51+0.023 -j.527
=-0.083-j3.367 kA
or .083 +j 3.367 to motor
Sum of these actual currents in phA is
=1.701-j32.87 -.083-j3.37
=1.618 -j 36.24 kA that is the actual fault current.
Top of page
Prob.9.8 | Line-to-line fault at the terminals of agenerator-To find fault current
The positive ,negative, and zero sequence reactances of a 15 MVA,11kV synchronous
generator are .3pu,.2pu, and.1pu respectively.The generator is solidly earthed and is
unloaded. A line-to-line fault occurs at the terminals of the generator.Determine the fault
current.
Solution: | The sequence network is shown below:
Ea
|  |  | Va1 |  | Va2
|  | Z1= j | 0.3 | pu Z2=j | 0.2 | pu
|  | Ia1 |  |  | Ia2
Assume that phases b and c are faulted.
| Let Ea= 1 | 0 deg.pu
For the line-line fault,
Ia=0
| Ia1=-Ia2 = 1 | 1 | 0 deg.
Z1+Z2
| Z1= |  | .3i
| Z2= |  | .2i
| Ia1=-Ia2 = |  | -2i
The fault current is Ib= Ib0+Ib1+Ib2=0+a*a.Ia1+aIa2
| a= |  | -0.5+0.866i
| a*a= |  | -0.5-0.866i
| Ib= |  | -3.464 | pu
| Base MVA= |  | 15
| BasekV(L-L)= |  | 11
| Base current= |  | 787.2962 | A
| Fault current= |  | -2727.194 | A | Answer
Top of page
Prob.9.9 | To find fault curent & voltages for a DLG fault at the terminals of an unloaded
generator
A double line to earth fault occurs at the unloaded generator terminals in Prob.8.8.
Calculate the fault current and the line voltages
Ea
|  |  | Va1 |  | Va2 |  | Va0
|  | Z1= j | 0.3 | pu Z2=j | 0.2 | Z0=j | 0.1
|  | Ia1 |  |  | Ia2 |  | Ia0
Assume that phases b and c are faulted to earth.
| Let Ea= 1 | 0 deg.pu
| Ea1= |  | 1
| Z1= |  | .3i
| Z2= |  | .2i
| Z0= |  | .1i
|  | Ia1= | Ea/(Z1+(Z0Z2/(Z1+Z2)))
|  | = | -2.72727272727272i |  | pu
| Va1= |  | Ea-Ia1Z1
|  |  | 0.181818181818184 |  | pu
| Va2=Va1 |  | 0.181818181818184 |  | pu
| Va0=Va1 |  | 0.181818181818184 |  | pu
| Ia2=Va2/Z2 |  | -0.90909090909092i |  | pu
| Ia0=Va0/Z0 |  | -1.81818181818184i |  | pu
The fault current to earth is Ib+Ic.
Ib+Ic= (Ia0+a*aIa1+a.Ia0)+(Ia0+a.Ia1+a*a.Ia2)
| = |  | 2*Ia0+(a+a*a)(Ia1+Ia2)
| = |  | 2Ia0-(Ia1+Ia2)
Since Ia=0, we may write Ia=Ia0+Ia1+Ia2=0
or,-(Ia1+Ia2)=Ia0.
Therefore , fault current = Ib+Ic=3 Ia0=
|  |  | -5.45454545454552i |  | pu
| Since Base current in Prob.9.8= |  |  | 787.3 | A
| Fault current= |  |  | -4294.36363636369i |  | A | Answer
The line voltages are calculated as follows:
| Va=3Va1= |  | 0.54545 |  | pu
| Vb=Vc= |  | 0
| Vab=Va= |  | 3.4641 |  | kV | Answer
| Vbc= |  | 0 |  |  | Answer
| Vca=Va= |  | 3.4641 |  | kV | Answer
Top of page