## Sheet1
E. Economic Dispatch
This module provides students with visual displays of the matrix approach to solve the economic
dispatch problem with the Newton method. The graph of each unit's I/O curve is shown as the
solution changes for a given demand level and for unit high and low limits. The student is shown
the equations as the solution progresses and is instruct as to what equations have to be added
and how to change the parameters for additional analysis.
COST CURVE COEFFICIENTS
| UNIT 1 | UNIT 2
quadratic | 0.0156 | 0.0185 | K/MWsqh
linear | 2.1875 | 2.4074 | K/MWh
constant | 120.31 | 740.74 | K
GENERATION RANGE
| MINIMUM | MAXIMUM
UNIT 1 | 200 | 350 | MW
UNIT 2 | 100 | 200 | MW
POWER DEMAND |  | 400 | MW
OPTIMAL SOLUTION
| P1 | 179.7669
| P2 | 220.7669
| lambda | 7.7962
phi
MESSAGES
CALCULATE |  |  | QUIT
Notes:
Cost curves
C1=A1+B1P1+C1P1*P1
C2=A2+B2P2+C2P2*P2
IC1=B1+2C1P1
IC2=B2+2C2P2
Optimal dispatch rule and the equality constraint gives
B1+2C1P1=B2+2C2P2
P1+P2=PD
Solve these equations for P1 &P2:
P1=C2Pd/(C1+C2)+(B2-B1)/(2*(C1+C2))
220.2331
P2=Pd-P1 |  |  | 179.7669
lambda
P1 | P2 | Lambda1 | Lambda2 | P
100 | 119.3946 | 6.825 | 6.825 | 219.3946
125.6378 | 100 |  | 6.1074 | 225.6378 | P1=(IC2-B1)/2C1
148.6378 | 119.3946 |  | 6.825 | 268.0324 | P2=(IC2-B2)/2C2
186.2981 | 151.1514 | 8 | 8 | 337.4494
200 | 162.7054 | 8.4275 | 8.4275 | 362.7054 | 2.4504 | 8.4275 | 371.1329
179.7669 | 220.7669 |  | 7.7962 | 400 | Given Demand
244.2276 | 200 | 9.8074 | 9.8074 | 444.2276 | IC2=B2+2*C2P2, P1=IC2-B1/2C1
250.4006 | 205.2054 | 10 | 10 | 455.606
314.5032 | 259.2595 | 12 | 12 | 573.7627
350 | 289.1919 | 13.1075 | 13.1075 | 639.1919
378.6058 | 313.3135 | 14 | 14 | 691.9193
P | 219.39 | 225.6378 | 268.0324 | 337.4494 | 362.7 | 400 | 444.2276 | 455.606
P1 |  | 125.63 | 148.63 | 186.3 | 200 | 179.7669 | 244.227 | 250.4
P2 |  | 100 | 119.39 | 151.15 | 162.71 | 220.7669 | 200 | 205.2
lambda |  | 6.107 | 6.825 | 8 | 5.9125 | 7.796 | 10 | 12
The optimal solutions here are given for specific minimum and maximum generations
of units 1 & 2. Your exercise is to write the program fro general minimum and maximum values
of generations for the two units